## Status
GPA Test Distribution RTU
Point Position | Description | Device | Point Index | Point Tag | Signal Reference | Description | SQL
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56 | PCB E Open | RTU | 1 | CISCO819_RTU:AV56 | CISCO819_RTU-AV1 | CISCO819 - RTU - PCB E Open | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 RTU'), 7, 'CISCO819_RTU:AV56', 'CISCO819_RTU-AV1', 'CISCO819 - RTU - PCB E Open', 1)
57 | RTU Control Board Fail | RTU | 2 | CISCO819_RTU:AV57 | CISCO819_RTU-AV2 | CISCO819 - RTU - RTU Control Board Fail | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 RTU'), 7, 'CISCO819_RTU:AV57', 'CISCO819_RTU-AV2', 'CISCO819 - RTU - RTU Control Board Fail', 1)
58
59
60
61
62
63
64
65 | 115kV AIM F Open | SEL451 BkB | 1 | CISCO819_SEL451_BKB:AV65 | CISCO819_SEL451_BKB-AV1 | CISCO819 - SEL451 BkB - 115kV AIM F Open | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV65', 'CISCO819_SEL451_BKB-AV1', 'CISCO819 - SEL451 BkB - 115kV AIM F Open', 1)
66 | 115kV RLB H Open | SEL451 BkB | 2 | CISCO819_SEL451_BKB:AV66 | CISCO819_SEL451_BKB-AV2 | CISCO819 - SEL451 BkB - 115kV RLB H Open | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV66', 'CISCO819_SEL451_BKB-AV2', 'CISCO819 - SEL451 BkB - 115kV RLB H Open', 1)
67 | 115/25kV Bank-B Trouble Alarms | SEL451 BkB | 3 | CISCO819_SEL451_BKB:AV67 | CISCO819_SEL451_BKB-AV3 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Trouble Alarms | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV67', 'CISCO819_SEL451_BKB-AV3', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Trouble Alarms', 1)
68 | 115/25kV Bank-B UVLS Scheme Disabled | SEL451 BkB | 4 | CISCO819_SEL451_BKB:AV68 | CISCO819_SEL451_BKB-AV4 | CISCO819 - SEL451 BkB - 115/25kV Bank-B UVLS Scheme Disabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV68', 'CISCO819_SEL451_BKB-AV4', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B UVLS Scheme Disabled', 1)
69 | 115/25kV Bank-B UF Scheme Disabled | SEL451 BkB | 5 | CISCO819_SEL451_BKB:AV69 | CISCO819_SEL451_BKB-AV5 | CISCO819 - SEL451 BkB - 115/25kV Bank-B UF Scheme Disabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV69', 'CISCO819_SEL451_BKB-AV5', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B UF Scheme Disabled', 1)
70 | 115/25kV Bank-B L.S. Gnd Trip Disabled | SEL451 BkB | 6 | CISCO819_SEL451_BKB:AV70 | CISCO819_SEL451_BKB-AV6 | CISCO819 - SEL451 BkB - 115/25kV Bank-B L.S. Gnd Trip Disabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV70', 'CISCO819_SEL451_BKB-AV6', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B L.S. Gnd Trip Disabled', 1)
71 | 115/25kV Bank-B Low Oil Trip Disabled | SEL451 BkB | 7 | CISCO819_SEL451_BKB:AV71 | CISCO819_SEL451_BKB-AV7 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Low Oil Trip Disabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV71', 'CISCO819_SEL451_BKB-AV7', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Low Oil Trip Disabled', 1)
72 | 115/25kV Bank-B Arc Flash Trip Enabled | SEL451 BkB | 8 | CISCO819_SEL451_BKB:AV72 | CISCO819_SEL451_BKB-AV8 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Arc Flash Trip Enabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV72', 'CISCO819_SEL451_BKB-AV8', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Arc Flash Trip Enabled', 1)
73 | 115/25kV Bank-B Ext Flt (TOC,UF,UV,Arc,LS Gnd) | SEL451 BkB | 9 | CISCO819_SEL451_BKB:AV73 | CISCO819_SEL451_BKB-AV9 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Ext Flt (TOC,UF,UV,Arc,LS Gnd) | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV73', 'CISCO819_SEL451_BKB-AV9', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Ext Flt (TOC,UF,UV,Arc,LS Gnd)', 1)
74 | 115/25kV Bank-B Int Flt (587,Oil,50) | SEL451 BkB | 10 | CISCO819_SEL451_BKB:AV74 | CISCO819_SEL451_BKB-AV10 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Int Flt (587,Oil,50) | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV74', 'CISCO819_SEL451_BKB-AV10', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Int Flt (587,Oil,50)', 1)
75 | 115/25kV Bank-B UVLS Trip | SEL451 BkB | 11 | CISCO819_SEL451_BKB:AV75 | CISCO819_SEL451_BKB-AV11 | CISCO819 - SEL451 BkB - 115/25kV Bank-B UVLS Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV75', 'CISCO819_SEL451_BKB-AV11', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B UVLS Trip', 1)
76 | 115/25kV Bank-B UF Trip | SEL451 BkB | 12 | CISCO819_SEL451_BKB:AV76 | CISCO819_SEL451_BKB-AV12 | CISCO819 - SEL451 BkB - 115/25kV Bank-B UF Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV76', 'CISCO819_SEL451_BKB-AV12', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B UF Trip', 1)
77 | 115/25kV Bank-B 587 Trip | SEL451 BkB | 13 | CISCO819_SEL451_BKB:AV77 | CISCO819_SEL451_BKB-AV13 | CISCO819 - SEL451 BkB - 115/25kV Bank-B 587 Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV77', 'CISCO819_SEL451_BKB-AV13', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B 587 Trip', 1)
78 | 115/25kV Bank-B Low Oil Trip | SEL451 BkB | 14 | CISCO819_SEL451_BKB:AV78 | CISCO819_SEL451_BKB-AV14 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Low Oil Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV78', 'CISCO819_SEL451_BKB-AV14', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Low Oil Trip', 1)
79 | 115/25kV Bank-B Arc Flash Trip | SEL451 BkB | 15 | CISCO819_SEL451_BKB:AV79 | CISCO819_SEL451_BKB-AV15 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Arc Flash Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV79', 'CISCO819_SEL451_BKB-AV15', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Arc Flash Trip', 1)
80 | 115/25kV Bank-B 86T LOR Trip Coil Mon Alarm | SEL451 BkB | 16 | CISCO819_SEL451_BKB:AV80 | CISCO819_SEL451_BKB-AV16 | CISCO819 - SEL451 BkB - 115/25kV Bank-B 86T LOR Trip Coil Mon Alarm | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV80', 'CISCO819_SEL451_BKB-AV16', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B 86T LOR Trip Coil Mon Alarm', 1)
81 | 115/25kV Bank-B 87T C.O. (D Sw) | SEL451 BkB | 17 | CISCO819_SEL451_BKB:AV81 | CISCO819_SEL451_BKB-AV17 | CISCO819 - SEL451 BkB - 115/25kV Bank-B 87T C.O. (D Sw) | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV81', 'CISCO819_SEL451_BKB-AV17', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B 87T C.O. (D Sw) ', 1)
82 | 115/25kV Bank-B 86T LOR Trip | SEL451 BkB | 18 | CISCO819_SEL451_BKB:AV82 | CISCO819_SEL451_BKB-AV18 | CISCO819 - SEL451 BkB - 115/25kV Bank-B 86T LOR Trip | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV82', 'CISCO819_SEL451_BKB-AV18', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B 86T LOR Trip', 1)
83 | 115/25kV Bank-B Panel DC Fail | SEL451 BkB | 19 | CISCO819_SEL451_BKB:AV83 | CISCO819_SEL451_BKB-AV19 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Panel DC Fail | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV83', 'CISCO819_SEL451_BKB-AV19', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Panel DC Fail', 1)
84 | 115/25kV Bank-B Loss of Sta Serv AC Alarm | SEL451 BkB | 20 | CISCO819_SEL451_BKB:AV84 | CISCO819_SEL451_BKB-AV20 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Loss of Sta Serv AC Alarm | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV84', 'CISCO819_SEL451_BKB-AV20', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Loss of Sta Serv AC Alarm', 1)
85 | 115kV AIM F Trip Coil Mon Alarm | SEL451 BkB | 21 | CISCO819_SEL451_BKB:AV85 | CISCO819_SEL451_BKB-AV21 | CISCO819 - SEL451 BkB - 115kV AIM F Trip Coil Mon Alarm | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV85', 'CISCO819_SEL451_BKB-AV21', 'CISCO819 - SEL451 BkB - 115kV AIM F Trip Coil Mon Alarm', 1)
86 | 115kV AIM F DC Fail | SEL451 BkB | 22 | CISCO819_SEL451_BKB:AV86 | CISCO819_SEL451_BKB-AV22 | CISCO819 - SEL451 BkB - 115kV AIM F DC Fail | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV86', 'CISCO819_SEL451_BKB-AV22', 'CISCO819 - SEL451 BkB - 115kV AIM F DC Fail', 1)
87 | 115kV AIM F SC Sw | SEL451 BkB | 23 | CISCO819_SEL451_BKB:AV87 | CISCO819_SEL451_BKB-AV23 | CISCO819 - SEL451 BkB - 115kV AIM F SC Sw | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV87', 'CISCO819_SEL451_BKB-AV23', 'CISCO819 - SEL451 BkB - 115kV AIM F SC Sw ', 1)
88 | 115kV AIM F Test Sw Pos Test | SEL451 BkB | 24 | CISCO819_SEL451_BKB:AV88 | CISCO819_SEL451_BKB-AV24 | CISCO819 - SEL451 BkB - 115kV AIM F Test Sw Pos Test | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV88', 'CISCO819_SEL451_BKB-AV24', 'CISCO819 - SEL451 BkB - 115kV AIM F Test Sw Pos Test', 1)
89 | 115kV RLB H SC Sw | SEL451 BkB | 25 | CISCO819_SEL451_BKB:AV89 | CISCO819_SEL451_BKB-AV25 | CISCO819 - SEL451 BkB - 115kV RLB H SC Sw | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV89', 'CISCO819_SEL451_BKB-AV25', 'CISCO819 - SEL451 BkB - 115kV RLB H SC Sw ', 1)
90 | 115/25kV Bank-B SEL451 Password Failure | SEL451 BkB | 26 | CISCO819_SEL451_BKB:AV90 | CISCO819_SEL451_BKB-AV26 | CISCO819 - SEL451 BkB - 115/25kV Bank-B SEL451 Password Failure | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV90', 'CISCO819_SEL451_BKB-AV26', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B SEL451 Password Failure', 1)
91 | 25kV PCB E - Hot Line Tagged | SEL351 PCB E | 1 | CISCO819_SEL351_PCB_E:AV91 | CISCO819_SEL351_PCB_E-AV1 | CISCO819 - SEL351 PCB E - 25kV PCB E - Hot Line Tagged | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV91', 'CISCO819_SEL351_PCB_E-AV1', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Hot Line Tagged ', 1)
92 | 25kV PCB E - Recloser | SEL351 PCB E | 2 | CISCO819_SEL351_PCB_E:AV92 | CISCO819_SEL351_PCB_E-AV2 | CISCO819 - SEL351 PCB E - 25kV PCB E - Recloser | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV92', 'CISCO819_SEL351_PCB_E-AV2', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Recloser ', 1)
93 | 25kV PCB E - GND Trip Disabled | SEL351 PCB E | 3 | CISCO819_SEL351_PCB_E:AV93 | CISCO819_SEL351_PCB_E-AV3 | CISCO819 - SEL351 PCB E - 25kV PCB E - GND Trip Disabled | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV93', 'CISCO819_SEL351_PCB_E-AV3', 'CISCO819 - SEL351 PCB E - 25kV PCB E - GND Trip Disabled ', 1)
94 | 25kV PCB E - Supv. Disable | SEL351 PCB E | 4 | CISCO819_SEL351_PCB_E:AV94 | CISCO819_SEL351_PCB_E-AV4 | CISCO819 - SEL351 PCB E - 25kV PCB E - Supv. Disable | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV94', 'CISCO819_SEL351_PCB_E-AV4', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Supv. Disable ', 1)
95 | 25kV PCB E - Trip Coil Monitor | SEL351 PCB E | 5 | CISCO819_SEL351_PCB_E:AV95 | CISCO819_SEL351_PCB_E-AV5 | CISCO819 - SEL351 PCB E - 25kV PCB E - Trip Coil Monitor | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV95', 'CISCO819_SEL351_PCB_E-AV5', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Trip Coil Monitor ', 1)
96 | 25kV PCB E - Recloser Lockout | SEL351 PCB E | 6 | CISCO819_SEL351_PCB_E:AV96 | CISCO819_SEL351_PCB_E-AV6 | CISCO819 - SEL351 PCB E - 25kV PCB E - Recloser Lockout | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV96', 'CISCO819_SEL351_PCB_E-AV6', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Recloser Lockout ', 1)
97 | 25kV PCB E - Alt. Settings Applied | SEL351 PCB E | 7 | CISCO819_SEL351_PCB_E:AV97 | CISCO819_SEL351_PCB_E-AV7 | CISCO819 - SEL351 PCB E - 25kV PCB E - Alt. Settings Applied | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV97', 'CISCO819_SEL351_PCB_E-AV7', 'CISCO819 - SEL351 PCB E - 25kV PCB E - Alt. Settings Applied ', 1)
98 | Loss of Communication - Bank B SEL451 | RTU | 3 | CISCO819_RTU:AV98 | CISCO819_RTU-AV3 | CISCO819 - RTU - Loss of Communication - Bank B SEL451 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 RTU'), 7, 'CISCO819_RTU:AV98', 'CISCO819_RTU-AV3', 'CISCO819 - RTU - Loss of Communication - Bank B SEL451', 1)
99 | Loss of Communication - PCB E SEL351 | RTU | 4 | CISCO819_RTU:AV99 | CISCO819_RTU-AV4 | CISCO819 - RTU - Loss of Communication - PCB E SEL351 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 RTU'), 7, 'CISCO819_RTU:AV99', 'CISCO819_RTU-AV4', 'CISCO819 - RTU - Loss of Communication - PCB E SEL351', 1)
100 | SEL-451 TEST ONLY HLT PB8 | SEL451 BkB | 27 | CISCO819_SEL451_BKB:AV100 | CISCO819_SEL451_BKB-AV27 | CISCO819 - SEL451 BkB - SEL-451 TEST ONLY HLT PB8 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV100', 'CISCO819_SEL451_BKB-AV27', 'CISCO819 - SEL451 BkB - SEL-451 TEST ONLY HLT PB8', 1)
Note on B73: Bradley, Clarence: In cases with an OCB, this may be replaced with Low Air Pressure alarm rather than SF6 gas. 1/11 - CLB
Note on B75: Bradley, Clarence: Revised description to be consistent.3/11 clb
Note on B101: Bradley, Clarence: Revised description to be consisten. 3/11 clb

## Analogs
GPA Test Transmission RTU
Point Position | Point Description | Device | Point Index | Point Tag | Signal Reference | Description | SQL
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17 | 115/25kV Bank-B MW | SEL451 BkB | 28 | CISCO819_SEL451_BKB:AV17 | CISCO819_SEL451_BKB-AV28 | CISCO819 - SEL451 BkB - 115/25kV Bank-B MW | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV17', 'CISCO819_SEL451_BKB-AV28', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B MW', 1)
18 | 115/25kV Bank-B MVAR | SEL451 BkB | 29 | CISCO819_SEL451_BKB:AV18 | CISCO819_SEL451_BKB-AV29 | CISCO819 - SEL451 BkB - 115/25kV Bank-B MVAR | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV18', 'CISCO819_SEL451_BKB-AV29', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B MVAR', 1)
19 | 115/25kV Bank-B MVA | SEL451 BkB | 30 | CISCO819_SEL451_BKB:AV19 | CISCO819_SEL451_BKB-AV30 | CISCO819 - SEL451 BkB - 115/25kV Bank-B MVA | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV19', 'CISCO819_SEL451_BKB-AV30', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B MVA', 1)
20 | 115/25kV Bank-B Amps, Phase 3 | SEL451 BkB | 31 | CISCO819_SEL451_BKB:AV20 | CISCO819_SEL451_BKB-AV31 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV20', 'CISCO819_SEL451_BKB-AV31', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 3', 1)
21 | 115/25kV Bank-B Amps, Phase 2 | SEL451 BkB | 32 | CISCO819_SEL451_BKB:AV21 | CISCO819_SEL451_BKB-AV32 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV21', 'CISCO819_SEL451_BKB-AV32', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 2', 1)
22 | 115/25kV Bank-B Amps, Phase 1 | SEL451 BkB | 33 | CISCO819_SEL451_BKB:AV22 | CISCO819_SEL451_BKB-AV33 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV22', 'CISCO819_SEL451_BKB-AV33', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Phase 1', 1)
23 | 115/25kV Bank-B Volts, Phase 3 | SEL451 BkB | 34 | CISCO819_SEL451_BKB:AV23 | CISCO819_SEL451_BKB-AV34 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV23', 'CISCO819_SEL451_BKB-AV34', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 3', 1)
24 | 115/25kV Bank-B Volts, Phase 2 | SEL451 BkB | 35 | CISCO819_SEL451_BKB:AV24 | CISCO819_SEL451_BKB-AV35 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV24', 'CISCO819_SEL451_BKB-AV35', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 2', 1)
25 | 115/25kV Bank-B Volts, Phase 1 | SEL451 BkB | 36 | CISCO819_SEL451_BKB:AV25 | CISCO819_SEL451_BKB-AV36 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV25', 'CISCO819_SEL451_BKB-AV36', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Volts, Phase 1', 1)
26 | 115/25kV Bank-B Amps, Neutral | SEL451 BkB | 37 | CISCO819_SEL451_BKB:AV26 | CISCO819_SEL451_BKB-AV37 | CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Neutral | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV26', 'CISCO819_SEL451_BKB-AV37', 'CISCO819 - SEL451 BkB - 115/25kV Bank-B Amps, Neutral', 1)
27 | 25kV PCB E Megawatts | SEL351 PCB E | 8 | CISCO819_SEL351_PCB_E:AV27 | CISCO819_SEL351_PCB_E-AV8 | CISCO819 - SEL351 PCB E - 25kV PCB E Megawatts | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV27', 'CISCO819_SEL351_PCB_E-AV8', 'CISCO819 - SEL351 PCB E - 25kV PCB E Megawatts ', 1)
28 | 25kV PCB E MegaVARs | SEL351 PCB E | 9 | CISCO819_SEL351_PCB_E:AV28 | CISCO819_SEL351_PCB_E-AV9 | CISCO819 - SEL351 PCB E - 25kV PCB E MegaVARs | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV28', 'CISCO819_SEL351_PCB_E-AV9', 'CISCO819 - SEL351 PCB E - 25kV PCB E MegaVARs ', 1)
29 | 25kV PCB E Amps, Phase 3 | SEL351 PCB E | 10 | CISCO819_SEL351_PCB_E:AV29 | CISCO819_SEL351_PCB_E-AV10 | CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV29', 'CISCO819_SEL351_PCB_E-AV10', 'CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 3', 1)
30 | 25kV PCB E Amps, Phase 2 | SEL351 PCB E | 11 | CISCO819_SEL351_PCB_E:AV30 | CISCO819_SEL351_PCB_E-AV11 | CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV30', 'CISCO819_SEL351_PCB_E-AV11', 'CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 2', 1)
31 | 25kV PCB E Amps, Phase 1 | SEL351 PCB E | 12 | CISCO819_SEL351_PCB_E:AV31 | CISCO819_SEL351_PCB_E-AV12 | CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV31', 'CISCO819_SEL351_PCB_E-AV12', 'CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Phase 1', 1)
32 | 25kV PCB E Volts, Phase 3 | SEL351 PCB E | 13 | CISCO819_SEL351_PCB_E:AV32 | CISCO819_SEL351_PCB_E-AV13 | CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV32', 'CISCO819_SEL351_PCB_E-AV13', 'CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 3', 1)
33 | 25kV PCB E Volts, Phase 2 | SEL351 PCB E | 14 | CISCO819_SEL351_PCB_E:AV33 | CISCO819_SEL351_PCB_E-AV14 | CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV33', 'CISCO819_SEL351_PCB_E-AV14', 'CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 2 ', 1)
34 | 25kV PCB E Volts, Phase 1 | SEL351 PCB E | 15 | CISCO819_SEL351_PCB_E:AV34 | CISCO819_SEL351_PCB_E-AV15 | CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV34', 'CISCO819_SEL351_PCB_E-AV15', 'CISCO819 - SEL351 PCB E - 25kV PCB E Volts, Phase 1 ', 1)
35 | 25kV PCB E Amps, Ground | SEL351 PCB E | 16 | CISCO819_SEL351_PCB_E:AV35 | CISCO819_SEL351_PCB_E-AV16 | CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Ground | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL351 PCB E'), 7, 'CISCO819_SEL351_PCB_E:AV35', 'CISCO819_SEL351_PCB_E-AV16', 'CISCO819 - SEL351 PCB E - 25kV PCB E Amps, Ground ', 1)
36 | RRM "A" 25kV Line #4 - Volts, Phase 1 | JEMSTAR | 1 | CISCO819_JEMSTAR:AV36 | CISCO819_JEMSTAR-AV1 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV36', 'CISCO819_JEMSTAR-AV1', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 1 ', 1)
37 | RRM "A" 25kV Line #4 - Volts, Phase 2 | JEMSTAR | 2 | CISCO819_JEMSTAR:AV37 | CISCO819_JEMSTAR-AV2 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV37', 'CISCO819_JEMSTAR-AV2', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 2', 1)
38 | RRM "A" 25kV Line #4 - Volts, Phase 3 | JEMSTAR | 3 | CISCO819_JEMSTAR:AV38 | CISCO819_JEMSTAR-AV3 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV38', 'CISCO819_JEMSTAR-AV3', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Volts, Phase 3', 1)
39 | RRM "A" 25kV Line #4 - Amps, Phase 1 | JEMSTAR | 4 | CISCO819_JEMSTAR:AV39 | CISCO819_JEMSTAR-AV4 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 1 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV39', 'CISCO819_JEMSTAR-AV4', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 1', 1)
40 | RRM "A" 25kV Line #4 - Amps, Phase 2 | JEMSTAR | 5 | CISCO819_JEMSTAR:AV40 | CISCO819_JEMSTAR-AV5 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 2 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV40', 'CISCO819_JEMSTAR-AV5', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 2', 1)
41 | RRM "A" 25kV Line #4 - Amps, Phase 3 | JEMSTAR | 6 | CISCO819_JEMSTAR:AV41 | CISCO819_JEMSTAR-AV6 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 3 | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV41', 'CISCO819_JEMSTAR-AV6', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Amps, Phase 3', 1)
42 | RRM "A" 25kV Line #4 - Megawatts | JEMSTAR | 7 | CISCO819_JEMSTAR:AV42 | CISCO819_JEMSTAR-AV7 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Megawatts | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV42', 'CISCO819_JEMSTAR-AV7', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Megawatts', 1)
43 | RRM "A" 25kV Line #4 - MegaVARs | JEMSTAR | 8 | CISCO819_JEMSTAR:AV43 | CISCO819_JEMSTAR-AV8 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - MegaVARs | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV43', 'CISCO819_JEMSTAR-AV8', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - MegaVARs', 1)
44 | RRM "A" 25kV Line #4 - Power Factor | JEMSTAR | 9 | CISCO819_JEMSTAR:AV44 | CISCO819_JEMSTAR-AV9 | CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Power Factor | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 JEMSTAR'), 7, 'CISCO819_JEMSTAR:AV44', 'CISCO819_JEMSTAR-AV9', 'CISCO819 - JEMSTAR - RRM "A" 25kV Line #4 - Power Factor', 1)
45 | DC1 Voltage (output by relay as multiplied by 100?) | SEL451 BkB | 38 | CISCO819_SEL451_BKB:AV45 | CISCO819_SEL451_BKB-AV38 | CISCO819 - SEL451 BkB - DC1 Voltage (output by relay as multiplied by 100?) | INSERT INTO Measurement(DeviceID, SignalTypeID, PointTag, SignalReference, Description, Enabled) VALUES((SELECT ID FROM Device WHERE Name = 'CISCO819 SEL451 BkB'), 7, 'CISCO819_SEL451_BKB:AV45', 'CISCO819_SEL451_BKB-AV38', 'CISCO819 - SEL451 BkB - DC1 Voltage (output by relay as multiplied by 100?)', 1)