## APS Requirements (hidden)
# | Function | Internal Reference Section | ID | Event Data Retrieval Requirements | MoSCoW Prioritization | Yes/ No | If Yes, Please Explain
1 | Function | BFR-05 | 1 | The Distribution Management System (DMS) will automatically retrieve event records from digital relays. | Must have
2 | Function | BFR-06 | 2 | The DMS will automatically retrieve event records from fault recorders. | Must have
3 | Function | BFR-07 | 3 | The DMS will automatically retrieve transient records from digital relays. | Must have
4 | Function | BFR-08 | 4 | The DMS will automatically retrieve transient records from fault recorders. | Must have
5 | Function | BFR-09 | 5 | The DMS will automatically store event records from digital relays. | Must have
6 | Function | BFR-10 | 6 | The DMS will automatically store event records from fault recorders. | Must have
7 | Function | BFR-11 | 7 | The DMS will automatically store transient records from digital relays. | Must have
8 | Function | BFR-12 | 8 | The DMS will automatically store transient records from fault recorders. | Must have
9 | Function | BFR-13 | 9 | The DMS will automatically analyze event records from digital relay (Fault Location from Two Terminal Line). | Could have
10 | Function | BFR-14 | 10 | The DMS will automatically analyze event records from fault recorders (Fault Location from Two Terminal Line). | Could have
11 | Function | BFR-15 | 11 | The DMS will automatically analyze transient records from digital relays (Fault Location from Two Terminal Line). | Could have
12 | Function | BFR-16 | 12 | The DMS will automatically analyze transient records from fault recorders. | Could have
13 | Function | BFR-17 | 13 | The DMS will automatically push email notifications of event records from digital relays to System Operators. | Must have
14 | Function | BFR-18 | 14 | The DMS will automatically push email notifications of event records from fault recorders to System Operators. | Must have
15 | Function | BFR-19 | 15 | The DMS will automatically push email notifications of transient records from digital relays to System Operators. | Must have
16 | Function | BFR-20 | 16 | The DMS will automatically push email notifications of transient records from fault recorders to System Operators. | Must have
17 | Function | BFR-21 | 17 | The DMS will automatically push text notifications of event records from digital relays to System Operators. | Must have
18 | Function | BFR-22 | 18 | The DMS will automatically push text notifications of event records from fault recorders to System Operators. | Must have
19 | Function | BFR-23 | 19 | The DMS will automatically push text notifications of transient records from digital relays to System Operators. | Must have
20 | Function | BFR-24 | 20 | The DMS will automatically push text notifications of transient records from fault recorders to System Operators. | Must have
21 | Function | BFR-25 | 21 | The DMS will automatically push email notifications of event data to a defined set of On-call Duty System Protection Engineers. | Must have
22 | Function | BFR-26 | 22 | The DMS will automatically push email notifications of fault location data to a defined set of On-call Duty System Protection Engineers. | Must have
23 | Function | BFR-27 | 23 | The DMS will automatically push text notifications of event data to a defined set of On-call Duty System Protection Engineers. | Must have
24 | Function | BFR-28 | 24 | The DMS will automatically push text notifications of fault location data to a defined set of On-call Duty System Protection Engineers. | Must have
25 | Function | BFR-29 | 25 | The DMS will automatically push email notifications of event data to a defined set On-call Duty ECC Operators. | Must have
26 | Function | BFR-30 | 26 | The DMS will automatically push email notifications of fault location data to a defined set of On-call Duty ECC Operators. | Must have
27 | Function | BFR-31 | 27 | The DMS will automatically push text notifications of event data to a defined set of On-call Duty ECC Operators. | Must have
28 | Function | BFR-32 | 28 | The DMS will automatically push text notifications of fault location data to a defined set of On-call Duty ECC Operators. | Must have
29 | Function | BFR-33 | 29 | The DMS will automatically push email notifications of event data to a defined set of On-call Duty DOC Personnel. | Must have
30 | Function | BFR-34 | 30 | The DMS will automatically push email notifications of fault location data to a defined set of On-call Duty DOC Personnel. | Must have
31 | Function | BFR-35 | 31 | The DMS will automatically push text notifications of event data to a defined set of On-call Duty DOC Personnel. | Must have
32 | Function | BFR-36 | 32 | The DMS will automatically push text notifications of fault location data to a defined set of On-call Duty DOC Personnel. | Must have
33 | Function | BFR-37 | 33 | The DMS will automatically push email notifications of event data to a defined set of On-call Duty System Health Engineers. | Must have
34 | Function | BFR-38 | 34 | The DMS will automatically push email notifications of fault location data to a defined set of On-call Duty System Health Engineers. | Must have
35 | Function | BFR-39 | 35 | The DMS will automatically push text notifications of event data to a defined set of On-call Duty System Health Engineers. | Must have
36 | Function | BFR-40 | 36 | The DMS will automatically push text notifications of fault location data to a defined set of On-call Duty System Health Engineers. | Must have
| Non-Functional |  | 37 | Notifications sent out with 10 minutes of event occuring | Must have
37 | Function | BFR-41 | 38 | The DMS will enable remote access to microprocessor relays via Conventional access type. --------------- • TAPI connection An engineer will have access to relays or IEDs connected to that device. | Must have
38 | Function | BFR-42 | 39 | The DMS will enable remote access to microprocessor relays via Access Type 1. --------------- • SSH connection An engineer will have access to all relays at the site. | Could have
39 | Function | BFR-43 | 40 | The DMS will enable remote access to microprocessor relays via Access Type 2. --------------- • SSH connection An engineer will have access to the relays at the site. | Could have
40 | Function | BFR-44 | 41 | The DMS will enable remote access to microprocessor relays via Access Type 3. --------------- • Telnet connection An engineer will have access to relays or IEDs connected to that device. | Could have
41 | Function | BFR-45 | 42 | The DMS will enable remote access to microprocessor relays via Access Type 4. --------------- • PowerWAN network (PowWAN) • SSH connection An engineer will have access to all relays. | Should have
42 | Function | BFR-46 | 43 | The DMS will enable remote access to microprocessor relays via Access Type 5 --------------- • PowerWAN network • Telnet connection An engineer will have access to the relays. | Could have
43 | Function | BFR-47 | 44 | The DMS will enable remote access to microprocessor relays via Access Type 6. --------------- • CIMZ network • SSH connection An engineer will have access to the relays. | Must have
44 | Function | BFR-48 | 45 | The DMS will enable remote access to microprocessor relays via Access Type 7. --------------- • CIMZ network • Telnet connection An engineer will have access to relays or IEDs connected to that device. | Must have
45 | Function | BFR-49 | 46 | The DMS will enable remote access to microprocessor relays via Engineering Access Via SEL-3620. --------------- • Authentication through LDAP An engineer will have Read only, Read/Write, or Admin access to relays (CIP assets). In non-CIP substations, the SEL-3620 will authenticate individual access through a shared admin account before granting them access to relays. | Must have
46 | Function | BFR-50 | 47 | The DMS will allow a server to have access to all PWAN network connected event recording devices. | Should have
47 | Function | BFR-51 | 48 | The DMS will allow a server to have access to all SPNET network connected event recording devices. | Must have
48 | Function | BFR-52 | 49 | The DMS will allow a server to have access to all NGN network connected event recording devices. | Must have
49 | Function | BFR-53 | 50 | The DMS will allow a server to have access to all CIMZ network connected event recording devices. | Must have
| Non-Functional | BNFR-01 | 51 | The DMS will allow a server to retain event data for a minimum of one year. Ability to export event data | Must have
| Non-Functional |  | 52 | Archive data 5-10 years | Should have
| Function | BFR-54 | 53 | The DMS will monitor connectivity between the DMS, relays, and Digital Fault Reporters (DFRs) in the field. | Must have
| Function | BFR-55 | 54 | The DMS will alarm when there is no connectivity between the DMS, relays and DFRs in the field. | Must have
| Function | BFR-56 | 55 | The DMS will enable “listen” mode configuration when collecting event records. | Could have
| Function |  | 56 | Push notification for any loss of connectivity alarming within the DMS - email/text - relays/DFRs | Must have
| Function |  | 57 | The DMS will have a hierarchy that matches the PowerBase hierarchy (Substation name > feeder number > operating number). | Must have
| Function | BFR-58 | 58 | The DMS will allow a server to identify if a specific asset (distribution feeder device(s), 69 KV line, etc). is effected by a Non-Fault Event. | Must have
| Function | BFR-61 | 59 | The event data retrieved by the DMS includes the date of an event. The DMS will parse data and display date and time of the event | Should have
| Function | BFR-62 | 60 | The event data retrieved by the DMS includes the time of an event. | Should have
| Function | BFR-71 | 61 | The DMS will have the ability to organize data into folders based on a descending hierarchy of substation, asset, device. | Must have
| Function | BFR-72 | 62 | The DMS will pull event data from devices from a variety of manufacturers. | Must have
| Function | BFR-73 | 63 | The system will allow a server to identify if a specific distribution feeder device(s) is effected by an [additional event types] Event. | Must have
| Function | BFR-74 | 64 | The system will allow a server to identify if a specific distribution feeder device(s) is effected by a [event type]. | Must have
| Function | BFR-75 | 65 | The system will allow for a Wordbits element to be engaged that triggers tripping of device. | Must have
| Function | BFR-76 | 66 | The system will allow for a 50P element to be engaged that triggered tripping of device ground elements. | Must have
| Function | BFR-77 | 67 | The system will allow for a 51P element to be engaged that triggers tripping of device ground elements. | Must have
| Function | BFR-78 | 68 | The system will allow for a time-overcurrent element engaged that triggers tripping of device. | Must have
| Function | BFR-79 | 69 | The system will allow for a instantaneous element engaged that triggers tripping of device. | Must have
| Function | BFR-80 | 70 | The system will allow for a Single Phase fault type Line to Ground, LG combination to be engaged that triggers tripping of device | Must have
| Function | BFR-81 | 71 | The system will allow for a Two Phase, Phase to Phase, fault type Line to Line (LL) combination, to be engaged that triggers tripping of device | Must have
| Function | BFR-82 | 72 | The system will allow for a Two Phase, Phase to Phase, fault type Line to Line (LL) combination, to be engaged that triggers tripping of device | Must have
| Function | BFR-83 | 73 | The system will allow for a Three Phase Fault Type, Line to Line to Line (LLL) combination, to be engaged that triggers tripping of device | Must have
| Function | BFR-84 | 74 | The system will allow for a Three Phase Fault Type, Line to Line to Ground (LLG) combination, to be engaged that triggers tripping of device | Must have
| Function | BFR-85 | 75 | Ability to search past events based on any of the available data. | Must have
| Function | BFR-86 | 76 | Ability to filter past events based on any of the available data. | Must have
| Function | BFR-87 | 77 | The system will send a report by the following day at 9 am AZ Time when an event has occurred. | Could have
|  | BFR-88 | 78 | Ability to generate a report with specified information | Must have
|  | BFR-89 | 79 | The DMS will enable a minimum of 6 concurrent users. | Must have
|  | BFR-90 | 80 | The DMS will have the ability to create different user types. | Could have
|  | BFR-94 | 81 | REST Interface supported | Should have
|  | BFR-95 | 82 | API Interface | Should have
|  | BFR-98 | 83 | The DMS will retrieve Sequence of Events (SOE) data SER.txt file pull equivalent file | Must have
|  | BFR-99 | 84 | The DMS will retrieve Fault reports HIS.txt file. | Must have
|  | BFR-100 | 85 | The DMS will retrieve Oscillography files .eve (SEL Syncrowave) file. | Must have
|  | BFR-103 | 86 | The DMS will have the ability to be configured to “polling” mode. | Should have
|  | BFR-104 | 87 | When DMS is configured to “polling” mode polling interval will be programmable. | Should have
|  | BFR-105 | 88 | The DMS will be capable of performing transmission fault location analytics. | Should have
|  | BFR-106 | 89 | The software will enable two terminal fault location methodology. | Should have
89
90
91
92
93
94
95
96
97
98
99
100
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130
131
132
133
134
135
136
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151
152
153
154
155
156
157
158
159
160
161
162
163
164
165
166
167
168
169
170
171
172
173
174
175
176
177
178
179
180
181
182
183
184
185
186

## AutoEventReqs
# | BR Type | Internal Reference Section | ID | Event Data Retrieval Requirements | MoSCoW Prioritization | Yes/ No | If Yes, Please Explain
1 | BFR-01 | Function | 1 | The Automatic Event Retrieval System (AERS) will automatically retrieve event records from digital relays. | Must have | Yes | openMIC can retrieve event and transient records from relays, and DFRs.
2 | BFR-02 | Function | 2 | The AERS will automatically retrieve event records from fault recorders. | Must have | Yes | openMIC can retrieve event and transient records from relays, and DFRs.
3 | BFR-03 | Function | 3 | The AERS will automatically retrieve transient records from digital relays. | Must have | Yes | openMIC can retrieve event and transient records from relays, and DFRs.
4 | BFR-04 | Function | 4 | The AERS will automatically retrieve transient records from fault recorders. | Must have | Yes | openMIC can retrieve event and transient records from relays, and DFRs.
5 | BFR-05 | Function | 5 | The AERS will pull event data from devices from a variety of manufacturers. | Must have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
6 | BFR-06 | Function | 6 | The AERS will automatically store event records from digital relays. | Must have | Yes | Record storage location is configurable to any location the service has been granted access.
7 | BFR-07 | Function | 7 | The AERS will automatically store event records from fault recorders. | Must have | Yes | Record storage location is configurable to any location the service has been granted access.
8 | BFR-08 | Function | 8 | The AERS will automatically store transient records from digital relays. | Must have | Yes | Record storage location is configurable to any location the service has been granted access.
9 | BFR-09 | Function | 9 | The AERS will automatically store transient records from fault recorders. | Must have | Yes | Record storage location is configurable to any location the service has been granted access.
10 | BFR-10 | Function | 10 | The AERS will automatically push email notifications of event records from digital relays to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
11 | BFR-11 | Function | 11 | The AERS will automatically push email notifications of event records from fault recorders to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
12 | BFR-12 | Function | 12 | The AERS will automatically push email notifications of transient records from digital relays to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
13 | BFR-13 | Function | 13 | The AERS will automatically push email notifications of transient records from fault recorders to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
14 | BFR-14 | Function | 14 | The AERS will automatically push text notifications of event records from digital relays to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
15 | BFR-15 | Function | 15 | The AERS will automatically push text notifications of event records from fault recorders to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
16 | BFR-16 | Function | 16 | The AERS will automatically push text notifications of transient records from digital relays to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
17 | BFR-17 | Function | 17 | The AERS will automatically push text notifications of transient records from fault recorders to System Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
18 | BFR-18 | Function | 18 | The AERS will automatically push email notifications of event data to a defined set of On-call Duty System Protection Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
19 | BFR-19 | Function | 19 | The AERS will automatically push email notifications of fault location data to a defined set of On-call Duty System Protection Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
20 | BFR-20 | Function | 20 | The AERS will automatically push text notifications of event data to a defined set of On-call Duty System Protection Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
21 | BFR-21 | Function | 21 | The AERS will automatically push text notifications of fault location data to a defined set of On-call Duty System Protection Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
22 | BFR-22 | Function | 22 | The AERS will automatically push email notifications of event data to a defined set On-call Duty ECC Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
23 | BFR-23 | Function | 23 | The AERS will automatically push email notifications of fault location data to a defined set of On-call Duty ECC Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
24 | BFR-24 | Function | 24 | The AERS will automatically push text notifications of event data to a defined set of On-call Duty ECC Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
25 | BFR-25 | Function | 25 | The AERS will automatically push text notifications of fault location data to a defined set of On-call Duty ECC Operators. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
26 | BFR-26 | Function | 26 | The AERS will automatically push email notifications of event data to a defined set of On-call Duty DOC Personnel. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
27 | BFR-27 | Function | 27 | The AERS will automatically push email notifications of fault location data to a defined set of On-call Duty DOC Personnel. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
28 | BFR-28 | Function | 28 | The AERS will automatically push text notifications of event data to a defined set of On-call Duty DOC Personnel. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
29 | BFR-29 | Function | 29 | The AERS will automatically push text notifications of fault location data to a defined set of On-call Duty DOC Personnel. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
30 | BFR-30 | Function | 30 | The AERS will automatically push email notifications of event data to a defined set of On-call Duty System Health Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
31 | BFR-31 | Function | 31 | The AERS will automatically push email notifications of fault location data to a defined set of On-call Duty System Health Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
32 | BFR-32 | Function | 32 | The AERS will automatically push text notifications of event data to a defined set of On-call Duty System Health Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
33 | BFR-33 | Function | 33 | The AERS will automatically push text notifications of fault location data to a defined set of On-call Duty System Health Engineers. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
34 | BFR-34 | Function | 34 | The AERS will monitor connectivity between the AERS, relays, and Digital Fault Recorder (DFRs) in the field. | Must have | Yes | Connectivity is reported each polling cycle.
35 | BFR-35 | Function | 35 | The AERS will alarm when there is no connectivity between the AERS, relays and DFRs in the field. | Must have | Yes | Alarms can be configured for a variety of conditions, including connectivity, configuration changes, and diagnostics.
36 | BFR-36 | Function | 36 | The AERS will enable push notification for any loss of connectivity alarming within the AERS to relays via email. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
37 | BFR-37 | Function | 37 | The AERS will enable push notification for any loss of connectivity alarming within the AERS to relays via text. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
38 | BFR-38 | Function | 38 | The AERS will enable push notification for any loss of connectivity alarming within the AERS to DFRs via email. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
39 | BFR-39 | Function | 39 | The AERS will enable push notification for any loss of connectivity alarming within the AERS to DFRs via text. | Must have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
40 | BFR-40 | Function | 40 | The AERS will have the ability to organize data into folders based on a descending hierarchy of substation > asset > device. | Must have | Yes | Folder heirarchy is configurable.
41 | BFR-41 | Function | 41 | The AERS will enable a support link to be accessed by specific applications that grant access to the system directly. | Must have | Yes | Access management is done through Azure/Microsoft AD, hosted and controlled by APS.
42 | BFR-42 | Function | 42 | The AERS will enable search of past events based on any of the available data. | Must have | Yes | PQ Browser allows a search/browse of events based on filters of available event data.
43 | BFR-43 | Function | 43 | The AERS will filter past events based on any of the available data. | Must have | Yes | PQ Browser allows a search/browse of events based on filters of available event data.
44 | BFR-44 | Function | 44 | The AERS will generate a report with specified information. | Must have | Yes | Various reports can be exported, and the Notification platform can be configured to generate scheduled reports that are either sent as emails or saved as files to a designated file share.
45 | BFR-45 | Function | 45 | The AERS will enable mutliple users to connect concurrently. | Must have | Yes | There is no systematic limit on the number of concurrent users.
46 | BNFR-01 | Non-Functional | 46 | The AERS will allow a server to retain event data for 5-10 years. | Must have | Yes | There is no default storage limit or expiration.
47 | BFR-46 | Function | 47 | The AERS will retrieve Sequence of Events (SOE) data SER.txt file or equivalent file. | Must have | Yes | openMIC can be configured to retrieve SOE, Fault report, and Oscillography files
48 | BFR-47 | Function | 48 | The AERS will retrieve Fault reports HIS.txt file or equivalent file. | Must have | Yes | openMIC can be configured to retrieve SOE, Fault report, and Oscillography files
49 | BFR-48 | Function | 49 | The AERS will retrieve Oscillography files .eve (SEL Syncrowave) file or equivalent file. | Must have | Yes | openMIC can be configured to retrieve SOE, Fault report, and Oscillography files
50 | BFR-49 | Function | 50 | The AERS will enable remote access to microprocessor relays via "Conventional Access Type". | Must have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
51 | BFR-50 | Function | 51 | The AERS will enable remote access to microprocessor relays via "Access Type 6". | Must have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
52 | BFR-51 | Function | 52 | The AERS will enable remote access to microprocessor relays via "Access Type 7". | Must have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
53 | BFR-52 | Function | 53 | The AERS will allow a server to have access to all "SPNET network" connected event recording devices. | Must have | Yes | Applications are self-hosted so server and network access is managed by applicable policy enforcement.
54 | BFR-53 | Function | 54 | The AERS will allow a server to have access to all "NGN network" connected event recording devices. | Must have | Yes | Applications are self-hosted so server and network access is managed by applicable policy enforcement.
55 | BFR-54 | Function | 55 | The AERS will allow a server to have access to all "CIMZ network" connected event recording devices. | Must have | Yes | Applications are self-hosted so server and network access is managed by applicable policy enforcement.
56 | BFR-55 | Function | 56 | The AERS will parse data and display date of the event. | Should have | Yes | openXDA parses the data retrieved from the event record, including the date and time of the event, which are displayed in all of the suite's visualization tools.
57 | BFR-56 | Function | 57 | The event data retrieved by the AERS includes the time of an event. | Should have | Yes | openXDA parses the data retrieved from the event record, including the date and time of the event, which are displayed in all of the suite's visualization tools.
58 | BFR-57 | Function | 58 | The AERS will have the ability to be configured to “polling” mode. | Should have | Yes | openMIC "polls" a device and retrieves records when new records are available.
59 | BFR-58 | Function | 59 | When AERS is configured to “polling” mode polling interval will be programmable. | Should have | Yes | Polling setting schemas are configurable and able to be applied to devices en masse.
60 | BFR-59 | Function | 60 | The AERS will be capable of performing transmission fault location analytics. | Should have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
61 | BFR-60 | Function | 61 | The AERS will enable support of the API Interface. | Should have | Yes
62 | BFR-61 | Function | 62 | The AERS will enable two terminal fault location methodology. | Should have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
63 | BFR-62 | Function | 63 | The AERS will enable remote access to microprocessor relays via "Access Type 4". | Should have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
64 | BFR-63 | Function | 64 | The AERS will allow a server to have access to all "PWAN network" connected event recording devices. | Should have | Yes | Applications are self-hosted so server and network access is managed by applicable policy enforcement.
65 | BFR-64 | Function | 65 | The AERS will automatically analyze event records from digital relay (Fault Location from Two Terminal Line). | Could have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
66 | BFR-65 | Function | 66 | The AERS will automatically analyze event records from fault recorders (Fault Location from Two Terminal Line). | Could have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
67 | BFR-66 | Function | 67 | The AERS will automatically analyze transient records from digital relays (Fault Location from Two Terminal Line). | Could have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
68 | BFR-67 | Function | 68 | The AERS will automatically analyze transient records from fault recorders. | Could have | Yes | openXDA performs a variety of analytics on retrieved event data, including fault location and two terminal fault location.
69 | BFR-68 | Function | 69 | The AERS will enable remote access to microprocessor relays via "Access Type 1". | Could have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
70 | BFR-69 | Function | 70 | The AERS will enable remote access to microprocessor relays via "Access Type 2". | Could have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
71 | BFR-70 | Function | 71 | The AERS will enable remote access to microprocessor relays via" Access Type 3". | Could have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
72 | BFR-71 | Function | 72 | The AERS will enable remote access to microprocessor relays via "Access Type 5". | Could have | Yes | openMIC supports polling over a variety of connection types, including a number of proprietary protocols.
73 | BFR-72 | Function | 73 | The AERS will enable “listen” mode configuration when collecting event records. | Could have | Yes | openMIC "polls" a device and retrieves records when new records are available.
74 | BNFR-02 | Non-Functional | 74 | The AERS will send a report of captured event data by the following day at 9 am AZ Time when an event has occurred. | Could have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
75 | BNFR-03 | Non-Functional | 75 | The AERS will support role based user access. | Could have | Yes | Support for database, Windows, and Azure AD authentication.
76 | BNFR-04 | Non-Functional | 76 | The AERS will enable support of the REST Interface. | Could have | Yes
77 | BNFR-05 | Non-Functional | 77 | The AERS will send notifications within a maximum 10 mins. | Could have | Yes | Notifications (email and text, scheduled and triggered) can be configured and subscribed to (both assigned by admins and via self-subscription).
78 | BNFR-06 | Non-Functional | 78 | The AERS will enable export of event data. | Must have | Yes | Event data can be exported in CSV, PQDIF, or PQDS format.