## Master
REQUIREMENT
Software to retrieve event records from IEDs
Server to have access to all network connected event recording devices
Experience connecting to dial-up
Software to provide cyber security compliance including NERC CIP access
Software to be configured in “listen” mode.
Polling should be done on a reasonable interval that accommodates bandwidth capabilities
Recording device event data retrieval to include HIS, SOE, Oscillography
Event data can be delineated
Fault location analytics using two terminal fault location
Push notifications via email and text message of event data and fault location to a defined set of users
Event data to be retained for a period of 90 calendar days
System monitoring and alarming of available/unavailable relays.
Troubleshoot connectivity issues
Push notifications via email and text message of inaccessible IED alarms to a defined set of users
The AERS will have the ability to organize data into folders based on a descending hierarchy of substation
The AERS will enable a support link to be accessed by specific applications that grant access to the system directly
The AERS will enable search/filtering of past events based on any of the available data
The AERS will enable multiple users to connect concurrently
The AERS will send a report of captured event data by the following day at 9 am AZ Time when an event has occurred
The AERS will send notifications within a maximum 10 mins
The AERS will enable export of event data
Connect to terminal session
Compliance with APS Cybersecurity Controls
Evaluation of non-functional requirements