## Sheet1
RFI | Question | Vendor Response | Clarifications
General Information
1 | Company Background
1a | Please provide a brief history of your company, including years in operation and experience with Phasor Data Concentrators and Wide Area Measurement Systems. | Founded in 2010, GPA's first open source products were designed to support real-time synchrophasor data systems. These products were based on the Tennessee Valley Authority's 2009 open source release of the SuperPDC which had been in production use at TVA since 2004. The Department of Energy and FERC's Electric Reliability Organization, NERC sponsored projects to advance the use and secure sharing of synchrophasor data in the U.S. Since then, we have directly supported many utilities with their synchrophasor information needs. In 2013 GPA expanded its open source products to solve other utility information management problems. GPA Personel has a over 100 years of combined experience in the area of managing, collecting, storing and analyzing Synchrophasor data.
1b | What are your company's core competencies in the area of Phasor Measurement Units (PMUs) and PDCs/WAMS? | Data Management and Collection, including Concentration, transmission and storage. GPA also has the most comprehensive and adatable technology for managing synchrophasor data from the PMU to the End User.
2 | Product Overview
2a | Please provide a detailed description of your Phasor Data Concentrator solution | The openPDC is a high-performance data concentrator platform for managing streaming synchrophasor and other time-series data in real-time. The openPDC has been in production use since 2004. It has a proven performance record and continues to be on a steep improvement curve. Like all GPA products, the openPDC is open source, with no licensing costs so that the system can be easily tested prior to making production implementation commitments. The openPDC is much more than just a data concentrator, it is a flexible platform for processing high-speed time-series data that can adapt with changing technology to provide a future-proof phasor data architecture. The openPDC can be used to distribute data (both real-time and historical) to consuming applications and can be installed anywhere within the synchrophasor infrastructure, even on fanless computers that run in a substation environment. Although the primary purpose of the openPDC is concentration and management of real-time streaming synchrophasors, by having its functionality based on GPA's Time-Series Library the openPDC inherits a modular design that allows it to be classified as a generic event stream processor.
2b | What are the key features and capabilities of your PDC/WAMS system? | The openPDC implements a number of standard phasor protocols which can be used to receive data from devices. The supported protocols include IEEE C37.118, IEC 61850-90-5, IEEE 1344, BPA PDCstream, F-NET, SEL Fast Message, and Macrodyne among others. Using the Time-Series Library, the openPDC can be configured to archive to any historian system, however, the system also includes an available built-in historian, the openHistorian, for data archival. The local historian comes with a visualization and extraction tool, a high-speed local API and web services, all of which can be used to extract and monitor the data being archived in real-time. The files produced by the historian can also be analyzed using Hadoop. With version 2.1 or later, the openPDC can be deployed in POSIX environments as well as on Windows. Other features include: - Preemptive publishing to forward phasor data to receiving systems without the time delays required for time-synchronization. - Numerous TSL Adapters that are available through the Grid Solutions Framework. - Lossless phasor data transformation and replication with the ability to create a configurable number of output streams. - Extensive performance statistic history such as average latency, data quality and time code errors. - Generic configuration database with support for Microsoft SQL Server and Oracle as well as free alternatives such as MySQL and SQLite. - Distributed multi-node architecture supported for high availability and throughput. - Provided output adapters for multiple historians including the openHistorian, OSI-PI Historian and Hadoop. - Monitors and provides reports on synchrophasor data availability. - Includes a website hosted by the openPDC with a dashboard to show the operational status of each substation device that provides synchrophasor measurements.
Technical Specifications
3 | Data Handling
3a | What is the data throughput capacity of your PDC? | Depends on hardware. Systems with 2000+ PMUs are in use without any issues.
3b | How many PMU streams can your PDC handle simultaneously? Please make a distinction between the scenario's with and without waveform/POW data. | Server hardware dependent, no programmatic cap. | Assume 12 phasors per PMU and 3 analog values. Estimate for both 25 and 50 reports per second
3c | Describe the data aggregation and filtering capabilities of your PDC. | Data can be filtered through standard engineering checks (e.g. in range, non-zero, latched values, Timestamp reasonability etc), custom filters are supported. Data aggregation incudes common statistical quantities (such as mean, median, min/max) and supports custom expressions.
4 | Performance
4a | What are the latency specifications for data processing and forwarding? | Latency for processing and forwarding is hardware dependent. Usual deployments at specified size have < 200ms.
4b | What are the system requirements for optimal performance of your PDC? | System Memory: Min: 8 GB; Recommended: 32 GB CPU Resources: Minimum: 2 cores, 2 GHz; Recommended: 4+ cores, 3+ GHz Free Local Storage Space: Less than 20 GB
4c | How does your PDC handle data synchronization? | openPDC handles data synchronization through data concentration.
5 | Scalability
5a | Can your PDC scale to accommodate increasing data volumes and additional PMUs? | Yes
5b | Describe the scalability options and limitations of your PDC. | Limitations are hardware based. openPDC suports scaling via multi node systems as well as single node systems on increased hardware specifications.
| Data Processing and Calculation Capabilities |  | For data processing Capabilities, please indicate whether the analytics are available in the PDC or WAMS Application
6 | Data Processing
6a | What types of calculations can your PDC perform on incoming phasor data (e.g., power flow calculation, frequency calculation, voltage stability analysis, rotor angle stability and oscillation detection)? | The PDC supports Power Flow, Frequency computation, Sequence Computation, event. Optionally GPA offers a Oscillation detection and analysis package as an add-on.
6b | Describe the real-time data processing capabilities of your PDC. | openPDC is built around extensibility. Users can configure custom computations. Built in, out of the box functionality includes: Power Computation, Sequence Components, Oscillation Detection, Oscillation Analysis, Islanding Detection, Standard Alarming (threshold based), and Asset Health Analysis (SNR, Imbalance).
6c | Can your PDC handle custom calculations or user-defined algorithms? | Yes
6d | For each advanced function like voltage stability analysis, rotor angle stability and oscillation detection, specify the inputs, outputs, and the method. | Oscilation Detection is based on Frequency and Voltage/Current angles.
6e | Is there any license limitation on advanced functions (the number of instances each function can support)? | Licenses are provided on a per-environment basis, where an environment is defined as one or more instances monitoring the same data (e.g., Substation vs. Control Room, Transmission vs. Distribution, etc.) and an "instance" is defined as a separate installation (e.g., failover clusters; production, acceptance, and test; etc.).
6f | Does PDC-WAMS software support Fortescue transformation to calculate sequence values? | Yes
6g | Does PDC software support defining a reference PMU and calculating delta phase angles? | Yes
7 | Latency and Performance
7a | What is the typical latency for performing calculations on incoming data? | Depends on hardware and computation. Typically < 1s. For simple computations such as power, sequence, etc., < 200ms.
7b | How does your PDC ensure real-time processing of data and calculations? | The PDC uses standard synchronized time alignment with configurable latency thresholds.
7c | Are there performance benchmarks available for these calculation capabilities?
8 | Supported Calculations
8a | What pre-built calculation functions are available in your PDC (e.g. RMS calculation, phase angle difference)? | Phase Angle Difference, Frequency, Power, Sequence Components, SNR, Imbalance
8b | Can your PDC perform statistical analyses, such as moving averages or standard deviations, on the incoming data?
9 | Customizability
9a | Is there a scripting or programming interface available for adding custom calculations? | Yes
9b | What languages or environments (e.g., Python, MATLAB, custom scripting languages, ...) are supported for creating custom calculations? | Python, C#
9c | Can users upload and deploy their own calculation scripts or modules? | Yes
10 | Data Aggregation and Transformation
10a | How does your PDC aggregate data from multiple PMUs for composite calculations? | The PDC uses standard synchronized time alignment with configurable latency thresholds.
10b | Are there any built-in functions for data transformation and normalization? | yes
11 | Scalability of Calculations
11a | How does the PDC handle increasing volumes of data and additional calculation demands? | Hardware dependent
11b | Are there any limitations on the number or complexity of calculations that can be performed concurrently? | Hardware dependent
12 | Result Handling and Output
12a | How are the results of calculations managed and stored by your PDC? | The openPDC does not store Calculations; results of calculations are managed via routing, just like any other measurement entering the system. GPA offers the openHistorian as an option for storage. The openHistorian uses a file based high performance archive to store raw data and computation results.
12b | Can the results be visualized in real-time, exported, or integrated with other systems? Describe any APIs, supported API languages, supported queueing systems, other interfacing formats or export formats supported | Yes. The openHistorian includes a C# API, a Python API as well as a REST API. GPA also offers an excel add-on. The openHistorian can be integrated directly into Grafana, as well as output data in various protocols including ICCP, STTP, etc., or added to synchrophasor protocols.
12c | Is there the possibilty to start functionalities based on triggers on synchrophasor values or results of analysis? | Yes
12d | Is there a possibility to define different warning values on the synhcrophasor or post-processed values analyzed (e.g. on the damping or amplitude of oscillations) | Yes
12e | Is there a possibility to communicate different levels of alarms with different actions and level of verbosity w.r.t. the synchrophasor or post-processed data? | Yes
12f | Does the PDC support alerting and notifications based on calculated results, and how alerting/notifications can be sent out? | Yes, notifications can be sent out via SMS and/or email.
12g | Does the PDC-WAMS support trending capability for incoming data or calculated values? | Yes
12h | Does the PDC software support exchanging alarms and notifications with external systems and with which interfacing protocols? (if feasible, linked with "integration section" for technical implementation ). | Yes, the openPDC supports sending alarms out via ICCP, STTP, and other standard protocols.
12i | Does the PDC software support historical data playback on visualization functions? | Yes
12j | How many outputs your PDC can support to stream the outbound data? | Hardware dependent
12k | Does WAMS software process CIM and/or CIM-CGMES file and identify/represent network SLD? Does it show input and calculated data on the SLD?
12l | Does WAMS software support user manual data entry to updater network SLD?
13 | Documentation and Support
13a | Is there detailed documentation available for the calculation capabilities and custom scripting options of your PDC? | Yes
13b | What kind of support and resources are available for troubleshooting calculation-related issues? | GPA-offered maintenance support includes assistance troubleshooting any calculation-related issues via issue/request portal, phone, email, or on-site.
14 | Case Studies and References
14a | Can you provide examples or case studies where your PDC's calculation capabilities have been effectively utilized? | Yes
14b | Are there any customer testimonials or references that highlight the performance of these features? | Yes
Advanced Calculation and Post-processing Functionalities
15 | Algorithm for oscillation detection
15a | Is it possible to calculate the damping of an oscillation? | Yes
15b | Does the range (frequency) of oscillation has to be defined beforehands or does the algorithm is able to automatically detect undamped oscillation throughout an arbitrary range of frequency? | Yes | Yes to which?
15c | Does the algorithm allows detecting the amplitudes of the oscillations (in terms of frequency, voltage angle, active or reactive power)? | Yes
15d | Does the algorithm allows the detection of the participation factor and mode shape of a synchrophasor to an oscillation mode in the system? | Yes
15e | Is it possible to rank the participation factors of the different synchrophasors? | Yes
15f | Is there a technical limit (and what is it) to the range of frequency for which oscillations can be detected, provided sufficiently high resolution data is measured by the PMUs and transferred to the PDC? | Nyquist limitations apply dependent on the frequency of the PMUs. Typically algorithms work well at 5 Hz for 30FPS Data
15g | Is it possible to define arbitrary observables for the detection of badly damped oscillations such as reactive power and/or voltage magnitude and/or active and/or reactive power? | Yes
16 | POW and Waveforms data
16a | Is your PDC able to receive and elaborate POW/waveform data? | Yes
16b | Is your PDC able to elaborate offline or realtime POW data? | Yes
16c | Does your system allow the detection of oscillations or interaction in sub-synchronous or super-synchronous range? | No - Oscillation Detection is limited to PMU data
16d | What is the method used for detection of oscillations or interaction from higher resolution data (waveform/POW)? | N/A
16e | For which range of frequency it is possible to allow the detection of oscillations or interactions in the sub-synhcrounous or super synchronous range? | N/A
16f | Which protocols of communication are used to exchange higher time (waveforms/POW) resolution data than synhcrophasors? | DNP3, STTP (recommended)
16g | What is the frequency range maximum of detection of interaction you have implemented in a project?
16h | Are there additional tools available in your PDC/WAMS system for the analysis of Waveform/POW data? | GPA recommends use of our disturbance analytic products for POW data. This is separate from the WAMS systems.
Data Availability and KPI Features
17 | Data Availability Metrics
17a | What metrics does your PDC use to measure data availability? | % data available, % data within engineering reasonability limits
17b | How is data availability calculated and reported? | Data availability is reported as % data received over expected at given frame rates.
17c | Can you provide examples of typical data availability KPIs (e.g., uptime percentage)? | Uptime is dependent on Utility Hardware. We have deployed 99.9999% uptime systems.
18 | Real-Time Monitoring
18a | Does your PDC provide real-time monitoring of data streams and availability? | Yes
18b | Can the PDC alert administrators to data availability issues in real time? Is there a possibility to detect non working or problems with the communication of the PMUs? After detection, is it possible to create alarms or notifications? Can alarms/notifications be transferred to an external entity? (if feasible, linked with "integration section" for technical implementation ). | Yes. openPDC provides data availability and data integrity dashboards via Grafana and can alert based on these metrics
18c | What tools or dashboards are available for real-time data monitoring? (if feasible, linked with "integration section" for technical implementation ). | openPDC/openHistorian comes integrated with Grafana for real-time visualization
19 | Historical Data Analysis
19a | Does the PDC support historical data availability analysis? | Yes
19b | What tools are available for analyzing and reporting historical data availability trends? | openHistorian supports APIs and data export of historical trends, including data availability
19c | Can you provide examples of reports or visualizations that illustrate historical data availability? | Yes
20 | Redundancy and Failover Mechanisms
20a | What redundancy features are built into your PDC to ensure data availability? | Automated Archive Data Recovery ensures archive data completeness when connectivity to the substation is unavailable. It works by monitoring for gaps in the real-time data and requesting any missing data from the substation PDC's local historian once connectivity to the substation has been restored. Automated Connection Failover ensures data continuity when the substation PDC needs to go offline for maintenance, gets rebooted, or is unavailable for any reason. It works by temporarily bypassing the primary PDC data connection and directly connecting to the substation PMUs to ensure data keeps flowing.
20b | How does your PDC handle failover in case of hardware or software failures?
20c | Can you describe the process and performance of your PDC during a failover event?
20d | What redundancy features are built into your WAMS Application server to ensure applications availability?
21 | Data Integrity
21a | How does your PDC ensure data integrity during transmission and storage? | Depends on the protocol used. Network protocols typically include checksums and sync bytes. openHistorian writes to the local file system; errors will merely prevent it from writing data to the file.
21b | What error detection and correction mechanisms are in place? | Depends on the protocol used. TCP supports retransmission, but UDP-based protocols may accept data loss due to errors on a per-frame basis. Errors in openHistorian cause data to build up in the in-memory queue, and too much build-up will result in large chunks of data being lost to make room for more.
22 | Compliance and Standards
22a | Is your PDC compliant with any industry standards related to data availability and integrity (e.g., IEEE C37.118, NERC CIP)? | IEEE C37.118; NERC CIP; IEEE 2664;
22b | How does your PDC ensure compliance with these standards? | GPA actively participates in Standard development activity and continously updates our applications to comply with these standards
23 | Maintenance and Updates
23a | What is the maintenance schedule for your PDC, and how does it impact data availability? | openPDC is deployed on client systems. Clients can schedule updates based on their own requirements. Updates may require restarts. If failover systems are set up, no impact on data availability is expected.
23b | How are software updates and patches handled to minimize downtime? | Software updates can be scheduled with GPA support staff or on your own. We work with you to determine the best way to update based on your setup.
24 | Service Level Agreements (SLAs)
24a | What SLAs do you offer regarding data availability and uptime? | GPA offers various SLAs for resolving issues, but, due to the system being deployed on customer hardware, GPA does not offer data availability or uptime guarantees.
24b | Can you provide details on the penalties or remedies if the SLAs are not met? | Depend on specific agreement
25 | User Notifications and Alerts
25a | What notification and alerting mechanisms are available for data availability issues? | email and SMS
25b | Can users customize alerts based on specific data availability thresholds or conditions? | Yes
26 | Data Backup and Recovery
26a | What data backup solutions are provided with your PDC? | None. Backup is handled by customer infrastructure.
26b | How does the PDC handle data recovery in the event of a failure? | If Protocols used support data gap recovery, the PDC will attempt to recover missing data.
27 | Customer References and Case Studies
27a | Can you provide references from existing customers who use your PDC for critical data availability? | Yes
27b | Are there case studies available that demonstrate the effectiveness of your PDC's data availability features? | No case studies are available.
Compliance and Standards
28 | Standards Compliance
28a | Is your PDC compliant with IEEE C37.118 standards for synchrophasor measurements? | Yes
28b | What other industry standards does your PDC comply with? | EC 61850-90-5, IEEE 1344, BPA PDCstream, F-NET, SEL Fast Message, IEEE 2664, and Macrodyne
28c | What are the protocols are supported to exchange data with Waveform/POW devices? | DNP-3, ICCP, IEEE 2664, FTP, SEL Protocol, ION proprietary, Dranetz proprietary
28d | Does your PDC receive GNSS signal to be UTC time synchronized and in what formats? | No
28e | Does your PDC supports PTP? | Hardware dependent | Should this be "Yes, openPDC supports PTP so long as the hardware is capable."?
29 | Interoperability
29a | How does your PDC ensure interoperability with PMUs from different manufacturers? | openPDC ensures interoperability with PMUs from different manufaturers via use of standard protocols.
29b | Describe any compatibility issues with existing PMUs or other PDCs. | None that GPA is aware of
29c | Do you have a list of successful connected PMU models from other vendors to your PDC? | SEL, GE, Powerside, APP, Mehta Tech, Arbiter, Ametek, Macrodyne, Qualitrol, NxtPhase, FNET, SIMEAS
29d | Do you have a list of successful connected Waveform/POW models from other vendors to your PDC? | SEL, Schneider Electric ION, Powerside, APP, Mehta Tech, USI, Ametek (JEMStar), Dranetz
Security and Reliability
30 | Security Features
30a | What security measures are in place to protect data integrity and confidentiality? | Configuration and Data can be encrypted
30b | How does your PDC handle access control and user authentication? | Support for database, Windows, and Azure AD authentication.
30c | What cyber security measurements are required between PMUs and PDCs? | No requirements. GPA recommends standard cyber security practices, such as firewalls, encryption of traffic etc are employed
30d | What cyber security measurements are required between PDCs and WAMS? | No requirements. GPA recommends standard cyber security practices, such as firewalls, encryption of traffic etc are employed
31 | Reliability
31a | What redundancy and failover mechanisms are incorporated into your PDC?
31b | Can you provide details on the mean time between failures (MTBF) and system reliability?
Integration, Deployment and Architecture, Storage and Archiving
32 | Integration Capabilities
32a | How does your PDC and/or WAMS integrate with existing SCADA and EMS systems? | The openPDC can send and receive SCADA data via ICCP and other protocols. Also supports direct integration with OSI-PI and eDNA via vendor APIs.
32b | Describe the APIs, queueing systems or other interfaces available for integration. What protocols are supported? (e.g. IEC104, ...) What information can be exchanged (e.g alarm messages, notifications, ...) | ICCP, DNP3, etc. All data can be exchanges, including notifications, alarms and synchrophasor data
32c | Can the PDC down sample data to send to EMS? | Yes
32d | Does the PDC and/or WAMS software support browser-based access for cloud implementations? If yes, please elaborate on the cloud implementation capabilities and limitations. | Primary user interface is via web browser. Some configuration options require access to the openPDC Manager application on the installation server.
33 | Deployment
33a | What are the typical deployment times for your PDC and WAMS? | New deployments on new systems take approximately 1 week. Updates can be deployed in < 10 minutes per instance
33b | Describe the installation and commissioning process. | Customer Dependent. Typically GPA and customer personnel work together to determine best architecture, including failover capabilities, as needed. Then GPA provides hardware requirements and network requirements (including firewall changes needed). Once customer provisions required hardware, GPA works with customer IT/OT to install and configure systems and provide any necessary training. GPA continues to support customer engineers to develop any custom visualization and analytics as needed on an ongoing basis.
33c | What are the application server specifications of your PDC and WAMS? Minimum size, performance, supported operating systems (Windows Server, ...), supported database systems (MS SQL server, MongoDB, ...) | OS: Windows Server 2012 R2 or later, 64-bit Pre-installation requirements: .NET 4.8+ Supported Databases (for configuration data): • SQL Server (2012 or later; 2019 recommended, SQL Server Express is fine) • Oracle • MySQL • PostgreSQL • SQLite (no external install required) – not recommended for large deployments Officially Supported Browsers (for web admin): Chrome, Edge Hardware System Memory: Min: 8 GB; Recommended: 32 GB CPU Resources: Minimum: 2 cores, 2 GHz; Recommended: 4+ cores, 3+ GHz Free Local Storage Space: Less than 1 GB Networking Requirements: TCP 8500 for remote CLI; TCP 8220 for web admin
33d | Does the WAMS software support load balancing mechanism to scale by using multiple servers? | Yes
34 | Architecture
34a | Describe the functional split between the PDC and WAMS of your system. Which features are deployed in PDC and which ones in WAMS
34b | For e.g. 150 PMUs, what could be first indicative architecture? How many PDCs are required over Belgium, or can we centralize the PDC(s) over 2 locations in Belgium? Can the WAMS be centralized?
34c | What are typical bandwitdth needs per PMU (supporting POW) to take into account for a PMU-PDC connection (e.g. to calculate to total bandwidth required inbound per PDC)?
34d | What typical bandwidth is required between PDC and WAMS system (taking into account e.g. PMUs with Waveform/POW)? Are there any special network requirements between PDC and WAMS?
34e | What's the software setup of the PDC and WAMS solution? On premise TSO? Supporting TSO private cloud? SAAS? In case of SAAS, deployed and hosted within EEA (European Economic Area)? | On premise
35 | Data Storage and Archiving
35a | What is the data storage capacity of PDC? How can it be extended ? How many PMUs (the data of the PMUs) can be stored with this storage capacity and for how many days? (for a "non" Waveform/POW scenario and a Waveform/POW scenario, please mention the sample rate taken into account during your calculation for the POW scenario)
35b | Does the PDC support data compression to optimize the archiving capability? | Yes
35c | What's the typical storage architecture? 1 database or operational and archiving database? In case of an additional archiving server is used, what is the typical data storage capacity of the archiving server? How can it be extended ? How many PMUs (the data of the PMUs) can be stored and for how many days? (for a "non" waveform/POW scenario and a waveform/POW scenario, please mention the sample rate taken into account during your calculation for the waveform/POW scenario). What's the performance impact on the WAMS while consulting archived data?
35d | On what technology database technologies are supporting the data storage and archiving?
Support and Maintenance
36 | Support Services
36a | What types of support services do you offer (e.g., phone support, on-site support)? | Issue/request portal, phone, email, on-site
36b | What are your support hours and response times (expressed in CET time zone)? | Dependent on support agreement option: - Business Day (10 hour x 5 day) M-F 2pm-12am CET; 30 min response time - 24 hour x 7 day; 15 min response time
37 | Maintenance
37a | What are the regular maintenance requirements for your PDC? | Periodic security and improvement patches, approx. 6 month major release cycle.
37b | Do you offer software updates and patches? If so, how frequently are they released? | Yes; As needed
Cost and Licensing
38 | Pricing Structure
38a | What is the pricing model for your PDC (e.g., one-time purchase, subscription, dependancies number of PMUs, ...)? | Assuming this will be both PDC and Historian and not considering capex… Agreements are $20,000 USD annually per product, per environment, where an environment is defined as one or more instances monitoring the same data (e.g., Substation vs. Control Room, Transmission vs. Distribution, etc.) and an "instance" is defined as a separate installation (e.g., failover clusters; production, acceptance, and test; etc.). GPA offers a $5,000 USD discount per product for multiple products. This brings the total for the package (openPDC and openHistorian) to $30,000 annually. GPA also offers multi-year packages on request.
38b | Can you provide a detailed breakdown of costs, including licensing, maintenance, and support? | GPA maintenance and support contract includes licenses at no additional cost.
38d | Is the PDC software only or software and hardware | Software only
38e | What is the pricing model for the WAMS package? Are the application modules all included or they have individual price? | Assuming this will be both PDC and Historian and not considering capex… Agreements are $20,000 USD annually per product, per environment, where an environment is defined as one or more instances monitoring the same data (e.g., Substation vs. Control Room, Transmission vs. Distribution, etc.) and an "instance" is defined as a separate installation (e.g., failover clusters; production, acceptance, and test; etc.). GPA offers a $5,000 USD discount per product for multiple products. This brings the total for the package (openPDC and openHistorian) to $30,000 annually. GPA also offers multi-year packages on request.
39 | Licensing
39a | Describe the licensing terms and conditions for your PDC. | An annual maintenance agreement entitles the supported utility to the latest version of all features and improvement of the software on the subscribed environment, where an "environment" is defined as one or more instances monitoring the same data (e.g., Substation vs. Control Room, Transmission vs. Distribution, etc.) and an "instance is defined as a separate installation (e.g., failover clusters; production, acceptance, and test; etc.), during the period they are subscribed.
39b | Are there any additional costs for scaling or adding more PMUs? | No
References and Case Studies
40 | Customer References
40a | Can you provide references from existing customers using your PDC? | Yes
40b | Are there any case studies or success stories that demonstrate the effectiveness of your PDC?
40c | Are any of your PDCs or WAMS applications installed in Europe? | Yes
40d | Can you provide a customer list?
Additional Information
41 | Future Roadmap
41a | What are your future plans for the development and enhancement of your PDC? | Large overhaul of User Interface and addition of features coming 2025.
41b | How do you incorporate customer feedback into your product roadmap? | GPA holds an annual User's Group where users share experiences and wishlist features/improvements. In addition, users can submit requests through our support portal.
41c | Do you plan to support IEEE 2664-2024 Streaming Telemetry Transport Protocol, STTP? | Yes
41d | Does your PDC have an capability to support Point On Wave (POW) data? If yes please describe | Yes
41e | What are your future plans for the development and enhancement of your WAMS package?
42 | Customization
42a | Can your PDC be customized to meet specific requirements? | Yes
42b | Describe any customization options available.