## Sheet1
Section |  |  |  | Requirement | Meet Req? | Notes
3 Initial Setup | 3.1 Install Process |  |  | Installation Wizard
Does not require technician
Compatible with recent installation of Windows
Possible Linux
Does not require admin priveleges to install
| 3.2 Site Setup |  |  | Does not require admin priveleges to run
Adding devices is simple
Add devices individually and as group
Human-readable and configurable device name
|  | 3.2.1 Predefined Modbus Maps |  | Groups (with labels)
Predefined configuration for Satec devices
|  | 3.2.2 Generic Devices |  | Capability to add additional device configurations as Satec develops new devices
Allow for Modbus maps of generic devices
|  | 3.2.3 Thresholds |  | Allow user to save custom configurations
| 3.3 Communication Capabilities |  |  | Min/Max for each monitored value
Modbus over TCP/IP or Serially over COM ports
Analyze communication setup and notify the user of contradictions
If devices share same COM port but have different baud rates, contradiction should alert but not block
|  | 3.3.1 Modbus Addressing over TCP/IP |  | Support communication using ExpertPower Client
Modbus addressing should still be supported, allowing for multiple slaves to share same IP
If multiple slaves share same IP and port, software should not have multiple sockets open simultaneously
|  | 3.3.2 Satec ETCs |  | Software should close sockets when not in use
|  | 3.3.3 Other Protocols |  | Should allow for configuration of device wired through ETC https://www.satec-global.com/ETC-ONE-PLUS
4 Polling | 4.1 Scheduling |  |  | Additional protocols - nice to have
Custom polling frequency
Per device basis
Per value basis
Separate polling schedule for datalogs and device configuration
Ability to configure amount of time data is retained
Display expected storage requirements for specific configuration
| 4.2 Polled Values | 4.2.1 Basic Readings |  | Option to define max storage size - software estimate total log time for configuration
Voltage - Per Phase
Current - Per Phase (including I4 and Neutral where applicable)
THD Voltage and Current - Per Phase
Active Power, Reactive Power, Apparent Power, and Power Factor - Per Phase and total Frequency
Frequency
Present Volt Demand - Per Phase
Present Ampere Demand - Per Phase (Including I4 where applicable)
|  | 4.2.2 Energies |  | kW, kvar, kVA demands - Total
kWh and kvarh - import
kWh and kvarh - export
kWh and kvarh - net
|  | 4.2.3 Harmonics |  | kWh, kvarh and kVAh - total
Fundamental Magnitude Values for - V1, V2, V3, V4, I1, I2, I3, I4, kW L1, kW L2, kW L3, kvar L1, kvar L2, kvar L3, kVA L1, kVA L2, kVA L3, PF L1, PF L2, PF L3
Fundamental Phase Angles for - V1, V2, V3, V4, I1, I2, I3, I4s
|  | 4.2.4 Future Modifications |  | *Unless otherwise specified all values are 1 sec avg values
| 4.3 Data Log Retrieval |  |  | Allow for easy Modbus map updates
|  | 4.3.1 Communication Errors |  | Support for a subset of point IDs (ID value in the datalog) relevant to the application and display an error when encountering an unknown point ID
|  | 4.3.2 Timestamped Values |  | In the event of a lapse in comm., software should be able to fill in missing data from data log
|  | 4.3.3 Application Specific Datalogs (Optional Module) |  | Pull time-stamped data from device
Periodically poll application-specific Datalogs and generate reports
Power Quality (PQ) Event Log
Power Quality Compliance Reports, Statistics Report, and Harmonics Reports supporting bot IEC50160 and IEEE1159
Ability to export PQ reports in industry-standard file formats such as PQDIF and Comtrade
Event Log
Sequence of events (SOE) log
|  | 4.3.4 Waveforms |  | Fault (DFR) Log with distance to fault calculations
On devices that support waveforms, all waveform logs should be polled and stored
| 4.4 Configuration Information |  |  | Link event in respective record to the corresponding waveform
|  | 4.4.1 Device Information |  | Poll device for its configuration values
Device model ID - compare to configured device and provide mismatch warning
Device serial number - send notification if changed
|  | 4.4.2 Device Basic Setup |  | Device Firmware version and build number
Log configuration of: Wiring mode, PT ration, CT primary current, Nominal line frequency, Phase order, Power demand period, Number of demand periods in a sliding window, Power calculation mode
|  |  | 4.4.2.1 RTC Synchronization | Users with elevated priveleges should have ability to modify basic setup with device passwords
Software should poll RTC and store the drift giving the user the ability to view timestamps on the server
|  | 4.4.3 Device Faults |  | Ability to periodically update the on-device time, making use of the time zone registers on the device
5 Viewing Data | 5.1 Grouping and Hierarchy |  |  | Fault alerting
hierarchical display of devices
Filtering by labels
| 5.2 Graphical View |  |  | Save display config to a file for reuse later
Default view should be graphical dashboard of entire site with a key parameter displayed for each device or group.
|  | 5.2.1 Site View |  | Dashboards should be creatable in a user-friendly manner
Ability to add small widgets for each device
Ability to select avg, sum, min, max of children
Max and Min defined by user
|  | 5.2.2 Device View |  | Arithmetic formulas
|  |  | 5.2.2.1 Device Info | Click on device for device view
|  |  | 5.2.2.2 History | Basic information about the device
|  |  | 5.2.2.3 Diagnostics and Alarms | User configurable trend plot, histogram, or heat map of measured values
|  |  | 5.2.2.4 Phasor Diagram | Real time and historical diagnostics and alarms
|  |  | 5.2.2.5 Logs | Phasor diagram of all three phases (I4 when available), current and voltage
Option to view a list of data logs
|  | 5.2.3 Trend View |  | Ability to open data logs from the list
|  |  | 5.2.3.1 Delta Values | Easy way to generate graphs and plots from all measured values
|  |  | 5.2.3.2 Heat Maps | Bar graph of deltas between each point in trend plot
Values are displayed in a grid with a color scale
|  | 5.2.4 Custom Dashboards |  | Value for each box can be avg, min, max or delta for given time slot
| 5.3 List View |  |  | Sankey diagram for each parent in the device tree
Table of values for easy comparison and custom report generation
Export of tables to file formats compatible with common spreadsheet software
| 5.4 Waveform Viewer |  |  | Ability to store templates of different lists for quick and easy report generation
Poll and store waveforms
| 5.5 Report Tool |  |  | Ability to view multiple waveforms on either single or multiple plots
Method of generating reports of polled data
Ability to create custom reports from subsets of data
6 Events and Alarms | 6.1 Device Triggered Alarms (DFR - Extra Module) |  |  | Ability to save report templates
Ability to respond to device triggered alarms by polling relevant datalogs
|  | 6.1.1 Polled alarms |  | Ability to respond to device triggered alarms by initiating a user-defined alarm response
|  | 6.1.2 TCP Notification |  | Poll devices to detect a flag and respond accordingly to that event
Implement a Modbus server allowing the device to write to it
| 6.2 Software Triggered Alarms |  |  | When device initiates a TCP notification and writes to the Modbus server, the software should respond to the notification accordingly
| 6.3 Alarm Response |  |  | Ability to define formulas, conditions, and setpoints to trigger alarms based on measured values
7 Other Requirements | 7.1 Help Files |  |  | Ability to send emails and SMS in response to alarms
Built-in help files
Built-in tutorials
| 7.2 Firmware Updates and Device Configuration |  |  | Instructions available directly from applicable section without search
Ability to write to devices with basic config or firmware update
| 7.3 Complete Backup |  |  | Allow batch operation
Ability to store a complete backup including entire site config and all previously logged data
Automatic on configurable schedule
Option to backup only snapshots/deltas
| 7.4 Data Export |  |  | Can be used to migrate users from MDM to expert power
| 7.5 Site Import/Export |  |  | Export all polled data to common data file formats such as CSV, XML, and JSON
Ability to import/export site config
| 7.6 Run as a Service/Daemon |  |  | Text-based format (i.e., JSON) allowing for version control and diff
Starts automatically at boot
| 7.7 Encryption and Signed Data (Future) | 7.7.1 Encryption |  | Restarts in event of crash
|  | 7.7.2 Signed Data |  | Ability to communicate using an encrypted communication protocol (i.e., Secure Modbus)
Ability to read and confirm that read data is using an authentication protocol
| 7.8 Headless Operation |  |  | Ability to share data with third parties while maintaining authentication
|  | 7.8.1 Web Browser Interface |  | Ability to run on a server without HMI device
Exposes a subset of features using a webserver allowing remote access using a web browser
Require login and user access control
|  | 7.8.2 Command Line Interface (CLI) |  | Ability to disable web interface in case of security concerns
| 7.9 ExpertPower Client |  |  | Ability to remotely control software via CLI for users accessing via SSH or similar
| 7.10 Permissions and Usage Logs |  |  | Ability for devices that cannot be assigned a fixed IP to be identified by MAC address
User management and access control
Admin - Full Access
Privileged - full access but cannot create users or view usage logs
Operator - view all and modify communication settings, but cannot add or remove devices
User - view only values
| 7.11 Diagnostics and diagnostic logs |  |  | Timestamp logging for: failed access including username, successful logins and usage time, and changes made and by which user
| 7.12 Digital Twin (Future) |  |  | Include usage and diagnostic logs
| 7.13 Protocol Converter (Future) |  |  | Synchronize physical system to digital twin for continuous monitoring
8 Non-Technical Requirements | 8.1 Pricing Model |  |  | Serve as protocol converter allowing for other software systems that do not use Modbus
Ability to offer standalone license at onetime sale price
Additional module separate pricing
| 8.2 Support |  |  | 1 year of support included; no support or upgrades offered if annual package opted out
Ability to escalate issues to software provider
|  | 8.2.1 Termination of support |  | Clarify terms should software provider wish to no longer support