## Sheet1
Section |  |  |  | Requirement | Meet Req? | Notes
3 Initial Setup | 3.1 Install Process |  |  | Installation Wizard | y
|  |  |  | Does not require technician | y
|  |  |  | Compatible with recent installation of Windows | y
|  |  |  | Possible Linux | n
|  |  |  | Does not require admin priveleges to install | y
| 3.2 Site Setup |  |  | Does not require admin priveleges to run | y
|  |  |  | Adding devices is simple | y
|  |  |  | Add devices individually and as group |  | Possibly via SQL Script would need UI
|  |  |  | Human-readable and configurable device name | y
|  | 3.2.1 Predefined Modbus Maps |  | Groups (with labels) |  | Exists in openHistorian would need to be moved; low effor
|  |  |  | Predefined configuration for Satec devices |  | For other devices Yes, Would need to develop for SEATEC
|  | 3.2.2 Generic Devices |  | Capability to add additional device configurations as Satec develops new devices | y
|  |  |  | Allow for Modbus maps of generic devices | y
|  | 3.2.3 Thresholds |  | Allow user to save custom configurations | y
| 3.3 Communication Capabilities |  |  | Min/Max for each monitored value | y | Monitoring done in OpenHistorian allows this
|  |  |  | Modbus over TCP/IP or Serially over COM ports | y
|  |  |  | Analyze communication setup and notify the user of contradictions | y
|  |  |  | If devices share same COM port but have different baud rates, contradiction should alert but not block | y
|  | 3.3.1 Modbus Addressing over TCP/IP |  | Support communication using ExpertPower Client |  | Needs development
|  |  |  | Modbus addressing should still be supported, allowing for multiple slaves to share same IP | y
|  |  |  | If multiple slaves share same IP and port, software should not have multiple sockets open simultaneously | y
|  | 3.3.2 Satec ETCs |  | Software should close sockets when not in use | y
|  | 3.3.3 Other Protocols |  | Should allow for configuration of device wired through ETC https://www.satec-global.com/ETC-ONE-PLUS | y
4 Polling | 4.1 Scheduling |  |  | Additional protocols - nice to have | y
|  |  |  | Custom polling frequency | y
|  |  |  | Per device basis | y
|  |  |  | Per value basis |  | would need some development
|  |  |  | Separate polling schedule for datalogs and device configuration | y
|  |  |  | Ability to configure amount of time data is retained | y
|  |  |  | Display expected storage requirements for specific configuration | y
| 4.2 Polled Values | 4.2.1 Basic Readings |  | Option to define max storage size - software estimate total log time for configuration | y
|  |  |  | Voltage - Per Phase | y
|  |  |  | Current - Per Phase (including I4 and Neutral where applicable) | y
|  |  |  | THD Voltage and Current - Per Phase | y
|  |  |  | Active Power, Reactive Power, Apparent Power, and Power Factor - Per Phase and total Frequency | y
|  |  |  | Frequency | y
|  |  |  | Present Volt Demand - Per Phase | y
|  |  |  | Present Ampere Demand - Per Phase (Including I4 where applicable) | y
|  | 4.2.2 Energies |  | kW, kvar, kVA demands - Total | y
|  |  |  | kWh and kvarh - import | y
|  |  |  | kWh and kvarh - export | y
|  |  |  | kWh and kvarh - net | y
|  | 4.2.3 Harmonics |  | kWh, kvarh and kVAh - total | y
|  |  |  | Fundamental Magnitude Values for - V1, V2, V3, V4, I1, I2, I3, I4, kW L1, kW L2, kW L3, kvar L1, kvar L2, kvar L3, kVA L1, kVA L2, kVA L3, PF L1, PF L2, PF L3 | y
|  |  |  | Fundamental Phase Angles for - V1, V2, V3, V4, I1, I2, I3, I4s | y
|  | 4.2.4 Future Modifications |  | *Unless otherwise specified all values are 1 sec avg values | y
| 4.3 Data Log Retrieval |  |  | Allow for easy Modbus map updates | y
|  | 4.3.1 Communication Errors |  | Support for a subset of point IDs (ID value in the datalog) relevant to the application and display an error when encountering an unknown point ID | y
|  | 4.3.2 Timestamped Values |  | In the event of a lapse in comm., software should be able to fill in missing data from data log | y
|  | 4.3.3 Application Specific Datalogs (Optional Module) |  | Pull time-stamped data from device | y
|  |  |  | Periodically poll application-specific Datalogs and generate reports | y
|  |  |  | Power Quality (PQ) Event Log | y
|  |  |  | Power Quality Compliance Reports, Statistics Report, and Harmonics Reports supporting bot IEC50160 and IEEE1159 | y
|  |  |  | Ability to export PQ reports in industry-standard file formats such as PQDIF and Comtrade | y
|  |  |  | Event Log | y
|  |  |  | Sequence of events (SOE) log | y
|  | 4.3.4 Waveforms |  | Fault (DFR) Log with distance to fault calculations | y
|  |  |  | On devices that support waveforms, all waveform logs should be polled and stored | y
| 4.4 Configuration Information |  |  | Link event in respective record to the corresponding waveform | y
|  | 4.4.1 Device Information |  | Poll device for its configuration values | y
|  |  |  | Device model ID - compare to configured device and provide mismatch warning | y | MiMD currently, can move module
|  |  |  | Device serial number - send notification if changed | y | MiMD currently, can move module
|  | 4.4.2 Device Basic Setup |  | Device Firmware version and build number | y
|  |  |  | Log configuration of: Wiring mode, PT ration, CT primary current, Nominal line frequency, Phase order, Power demand period, Number of demand periods in a sliding window, Power calculation mode | y | MiMD currently, can move module
|  |  | 4.4.2.1 RTC Synchronization | Users with elevated priveleges should have ability to modify basic setup with device passwords |  | openMIC but not for SAETEC yet
|  |  |  | Software should poll RTC and store the drift giving the user the ability to view timestamps on the server | y
|  | 4.4.3 Device Faults |  | Ability to periodically update the on-device time, making use of the time zone registers on the device | y | openMIC but not for SAETEC yet
5 Viewing Data | 5.1 Grouping and Hierarchy |  |  | Fault alerting | y
|  |  |  | hierarchical display of devices | y
|  |  |  | Filtering by labels | y
| 5.2 Graphical View |  |  | Save display config to a file for reuse later | y
|  |  |  | Default view should be graphical dashboard of entire site with a key parameter displayed for each device or group. | y | PQDashboard Views would need to update PQDigest
|  | 5.2.1 Site View |  | Dashboards should be creatable in a user-friendly manner | y | SEBrowser
|  |  |  | Ability to add small widgets for each device | y | SEBrowser
|  |  |  | Ability to select avg, sum, min, max of children | y
|  |  |  | Max and Min defined by user | y
|  | 5.2.2 Device View |  | Arithmetic formulas | y
|  |  | 5.2.2.1 Device Info | Click on device for device view | y
|  |  | 5.2.2.2 History | Basic information about the device | y
|  |  | 5.2.2.3 Diagnostics and Alarms | User configurable trend plot, histogram, or heat map of measured values | y
|  |  | 5.2.2.4 Phasor Diagram | Real time and historical diagnostics and alarms | y
|  |  | 5.2.2.5 Logs | Phasor diagram of all three phases (I4 when available), current and voltage | y
Option to view a list of data logs
|  | 5.2.3 Trend View |  | Ability to open data logs from the list
|  |  | 5.2.3.1 Delta Values | Easy way to generate graphs and plots from all measured values
|  |  | 5.2.3.2 Heat Maps | [
Values are displayed in a grid with a color scale
|  | 5.2.4 Custom Dashboards |  | Value for each box can be avg, min, max or delta for given time slot
| 5.3 List View |  |  | Sankey diagram for each parent in the device tree
Table of values for easy comparison and custom report generation
Export of tables to file formats compatible with common spreadsheet software
| 5.4 Waveform Viewer |  |  | Ability to store templates of different lists for quick and easy report generation
Poll and store waveforms
| 5.5 Report Tool |  |  | Ability to view multiple waveforms on either single or multiple plots
Method of generating reports of polled data
Ability to create custom reports from subsets of data
6 Events and Alarms | 6.1 Device Triggered Alarms (DFR - Extra Module) |  |  | Ability to save report templates
Ability to respond to device triggered alarms by polling relevant datalogs
|  | 6.1.1 Polled alarms |  | Ability to respond to device triggered alarms by initiating a user-defined alarm response
|  | 6.1.2 TCP Notification |  | Poll devices to detect a flag and respond accordingly to that event
Implement a Modbus server allowing the device to write to it
| 6.2 Software Triggered Alarms |  |  | When device initiates a TCP notification and writes to the Modbus server, the software should respond to the notification accordingly
| 6.3 Alarm Response |  |  | Ability to define formulas, conditions, and setpoints to trigger alarms based on measured values
Ability to send emails and SMS in response to alarms
7 Other Requirements | 7.1 Help Files |  |  | Built-in help files
Built-in tutorials
| 7.2 Firmware Updates and Device Configuration |  |  | Instructions available directly from applicable section without search
Ability to write to devices with basic config or firmware update
| 7.3 Complete Backup |  |  | Allow batch operation
Ability to store a complete backup including entire site config and all previously logged data
Automatic on configurable schedule
Option to backup only snapshots/deltas
| 7.4 Data Export |  |  | Can be used to migrate users from MDM to expert power
| 7.5 Site Import/Export |  |  | Export all polled data to common data file formats such as CSV, XML, and JSON
Ability to import/export site config
| 7.6 Run as a Service/Daemon |  |  | Text-based format (i.e., JSON) allowing for version control and diff
Starts automatically at boot
| 7.7 Encryption and Signed Data (Future) | 7.7.1 Encryption |  | Restarts in event of crash
|  | 7.7.2 Signed Data |  | Ability to communicate using an encrypted communication protocol (i.e., Secure Modbus)
Ability to read and confirm that read data is using an authentication protocol
| 7.8 Headless Operation |  |  | Ability to share data with third parties while maintaining authentication
|  | 7.8.1 Web Browser Interface |  | Ability to run on a server without HMI device
Exposes a subset of features using a webserver allowing remote access using a web browser
Require login and user access control
|  | 7.8.2 Command Line Interface (CLI) |  | Ability to disable web interface in case of security concerns
| 7.9 ExpertPower Client |  |  | Ability to remotely control software via CLI for users accessing via SSH or similar
| 7.10 Permissions and Usage Logs |  |  | Ability for devices that cannot be assigned a fixed IP to be identified by MAC address
User management and access control
Admin - Full Access
Privileged - full access but cannot create users or view usage logs
Operator - view all and modify communication settings, but cannot add or remove devices
User - view only values
| 7.11 Diagnostics and diagnostic logs |  |  | Timestamp logging for: failed access including username, successful logins and usage time, and changes made and by which user
| 7.12 Digital Twin (Future) |  |  | Include usage and diagnostic logs
| 7.13 Protocol Converter (Future) |  |  | Synchronize physical system to digital twin for continuous monitoring
8 Non-Technical Requirements | 8.1 Pricing Model |  |  | Serve as protocol converter allowing for other software systems that do not use Modbus
Ability to offer standalone license at onetime sale price
Additional module separate pricing
| 8.2 Support |  |  | 1 year of support included; no support or upgrades offered if annual package opted out
Ability to escalate issues to software provider
|  | 8.2.1 Termination of support |  | Clarify terms should software provider wish to no longer support
General Note:
Proposal is modified openMIC with openHistorian to store data instead of writing to PQDif. Intergrated PQDigest for Visualization