Transmission Line Impedance Calibration

OpenECA Analytic Design Document

Chen Wang

11/10/2016

# Statement of Work

The analytic of transmission line impedance calibration is aiming to use linear Least Squares Estimation method to estimate the true line impedance of the whole power system given measurement error of the transducers. The alpha version of the program of this analytic firstly takes PSS\E simulated PMU measurements as input; then, analyzes the topology of the aimed power network; thirdly starting from one of the buses taken as the calibration starting bus that equipped with revenue PT and the corresponding line that equipped with revenue CT, conducts single transmission line impedance calibration; finally propagate the accuracy to the whole system based on its tree topology. The alpha version program is designed to be operating without openECA platform.

# Introduction

One of the ways to get the knowledge of the transmission lines’ impedances is to use the voltage and current measurements one get from the PMUs to conduct the Ohm Law. But as is shown in the previous analytic of CT/PT Calibration, such measurement would have ratio errors from the instrument transformers (CT/PTs) and the errors added by PMUs brought by the digitalization process. Both the errors brought by CT/PTs and PMUs is going to influence the accuracy of the calculation of the line. Therefore, one need to first know the components of the errors, then utilize estimation methods to find out the exact error to find the true impedances within the system.

# Transmission Line Impedance Calibration Methodology

## Measurement Data Flow

The actual voltages and currents of each single transmission line will firstly detected by the CT/PTs, and those values should be complex numbers and three-phase separately. Such transducers will inevitably add ratio errors which are also three-phases to those true values and send them to the PMUs. PMUs then are going to quantize each phase’s data and provide the positive sequence measurements to the energy management system after computation. The whole process is shown in Figure III-

Figure III-1. Voltage and Current Measurement Data Flow

The ratio errors, both three-phase separately and positive sequence, aforementioned are also complex values. For each single transmission line, the relationship among true values, measurements, and ratio errors is shown as in Figure III-2and equation (3.1).

Figure III-2. CT/PT Measurements Demonstration

where,  and  are the measurement of and true voltage on bus , respectively;  and  are the measurement of and true current flowing from bus  to bus , respectively;  and  are the ratio errors of voltage and currents on or flowing out of bus , respectively. The values on bus  are similar. All the values aforementioned are of positive sequence.

Accordingly, one can find the ratio correction factors , , , and  as follow

Such factors are equivalent to the ratio errors and will be used in the following calibration methodology.

However, for various phases, the ratio errors should be different. According to the IEEE C57.13-2016 standard, the ratio errors are as follows:

where  is the ratio error of phase A voltage measurement;  is the error magnitude, which should be within ;  is the error angle, which should be within . The ratio errors of the other two phases are respectively similar.

The CT/PTs will integrate ratio errors to the three-phase measurements separately. But the PMUs will provide positive sequence values. Therefore, taking voltage as example, the positive sequence voltage measurements would be as follow

where,  is the measured positive sequence voltage value; , , and  are the true values of three-phase voltages respectively;  is .

If the three-phase voltage measurements are balanced, namely

then,

Therefore, the positive sequence ratio error is

For the field data, the differences between three-phase measurements are less than 1%. Thus, as the three phases’ ratio errors keep constant, there is a constant positive sequence ratio error for each PMU measurements.

## PMU Quantization and Error

The PMUs installed on each 500KV buses within the system would provide time-stamped voltage and current measurements. According to the IEEE Std. C37.118, the digital signals output by PMUs are firstly quantized and then transferred to the positive sequence values. The quantization scale of the three-phase voltage measurements is 20V and that of the three-phase current measurements is 0.65A. Such results are based on the real PMU data

Some conclusions could be reached. Firstly, both the real and imaginary parts of the three single phases’ measurements are perfectly and separately quantized by the PMU because of its own characteristics.

Then the positive sequence measurements are thus approximately quantized. Take  as the quantization scale. The quantization error of the positive sequence values, i.e. , is uniformly distributed within  according to Theorem III 1.

Theorem III-1. If  is uniformly distributed in  then  is uniformly distributed in  for any  and .

Since the PMU quantization error is also uniformly distributed within a known range, the expectation of such error is 0 and therefore unbiased. During the estimation process, such 3-phase to positive sequence transfer error could be eliminated by conducting multiple times calibration and averaging the estimation results.

## Single Transmission Line Impedance Calibration Methodology

The single transmission line impedance calibration method is similar to the instrument transformer calibration method. We are also going to use the measured voltages and currents from both sides of the line to conduct the LSE algorithm. The estimation result is going to be the estimated impedance matrix .

However, the impedance and susceptance here is unknown and to be calculated. To simplify the calculation, two new variables are introduced as shown in equation .

With the entries of , we can calculate the estimated impedance and susceptance by compute estimated  firstly.

If we know the correction factors of the voltage and current measurements of the bus , the correction factors on bus  can then be calibrated as follow.

Then the estimated susceptance can be calculated as follow.

The single transmission line impedance can be calibrated as follow.

## System Propagation Methodology

The single line impedance calibration method can not only estimate the impedance and susceptance of the concerned transmission line, but also calibrate the correction factors of the instrument transformers on the other side of the line. However, this is based on the fact that both the  and  are known.

Since the voltage on one bus will always remain the same no matter measured from which line that connects to it, the bus voltage correction factor is chosen as the propagation media. Based on the aforementioned fact, we can find that if there are  lines that connected to the concerned bus  as in Figure III-3, the voltages measured by different PTs on those  lines should be as follow.

Figure III-3. Bus Voltage Injections

where,  is the true value of the voltage on bus ;  is the voltage correction factor of the PT measuring the voltage of bus  on line ;  is the voltage measurement of bus  on line  and .

Therefore, if we know one of the correction factors from the calibration of the previous line, we will be able to reach the true value of the voltage on the concerned bus. Thus we can calculate all the other ones and acquire enough information to calibrate the following lines.

In order to calculate all the ’s of current injections on the bus , we firstly need to know all the current injection measurements. A typical bus injection that has  lines connected to it can be shown as Figure III-4.

Figure III-4 Bus Current Injections Demonstration

If one of the correction factors, for example , is known, this equation can be written as

With the LSE method and the current injections measurements, the correction factors of all the other lines connected to the concerned bus can be estimated.

With such propagation method, if we can form the whole system into a tree topology, then all the CTs and PTs within such tree can be calibrated, given that the impedance as well as the susceptances are known and the existence of a redundant PT. The graphical searching method could be Breadth First Search(BFS) which is shown in Figure III-5. The numbers are the order based on which the nodes are visited.

Figure III-5. Breadth First Search Method

# Program Architecture (Alpha Version)

## Data Structure

The data structure of the alpha version controller is shown as follows:

## Data Flow

# Program Details (Alpha Version)

## Program Process

- PSS\E power system operation simulation

Use PSS\E to conduct power flow based on the IEEE 118-bus power system and the morning load pick-up curve to generate the voltages of the 345KV buses and currents flowing though corresponding transmission lines.

- Raw data processing

Read in CSV file generated by Python and PSS\E.

- Building error model (For test plan)

Add CT/PT measurement errors and PMU errors to the raw data of voltages and currents based on the derived error model; record the positive sequence errors and the true line impedance and susceptance.

- System topology analysis

Analyze the system topology based on the from-bus and to-bus information of the concerned lines; find the order of calibration propagation.

- Transmission line impedance calibration

Conduct the transmission line impedance calibration starting from the 345KV bus and corresponding line that equipped with revenue transducers; use the injection propagation method aforementioned to calibrate the whole 345KV system.

# Demonstration

## Raw Data Generation

In this section, the PSS\E simulation is conducted to generate voltage and current data of the concerned power system. The PSS\E is accessed through Python.

- Locate in to the folder maned as Step_1_VI_Acquisition; run the file IEEE_118_data_generation_main.py to start generating voltage and current measurements data.

- The generated voltage and current data can be found in the file named as VI_Measurement_All_345KV_Buses_Peak_PQI.csv; copy this file and paste it into the Step_2_Error Model folder.

## Error Model Construction

In this section, the CT/PT and PMU errors are added into the simulated data to construct the error model.

- Locate in to the folder maned as Step_2_Error Model. Run Matlab_CSV_adapter_IEEE_118.m through Matlab to acquire the bus information, voltage and current simulated data from the CSV file, VI_Measurement_All_345KV_Buses_Peak.csv; the results include

1) the 345KV bus number set, saved in Bus_number_set_345KV.mat,

2) the true values of the positive sequence voltages on each 345 KV buses, saved in V_true_value_positive_sequence.mat,

3) the true positive sequence currents flowing through all the lines, two-winding transformers, and three-winding transformers connected to the 345KV buses, saved in I_true_value_positive_sequence.mat, I_true_value_positive_sequence_trn.mat, and I_true_value_positive_sequence_gen.mat respectively,

4) the from-bus numbers and to-bus numbers of each transmission line, two-winding transformers, and three-winding transformers connected to the 345KV buses, saved in line_bus_info_all_lines.mat, line_bus_info_trn.mat, line_bus_info_gen.mat.

- Run Line_data_generation_IEEE_118.m through Matlab to acquire the power system network information, save the true value of the voltages and currents of each line or transformer equivalent line, and construct the error model introduced previously; the network information is saved in AC_line_info.mat which is formed as 11 column vectors, i.e. [line number, line ID, line type, from bus number, KV1, KI1, to bus number, KV2, KI2, Z, y], as well as the bus number information of all the 345KV transmission lines, saved in line_bus_info_345KV.mat; each transmission line or transformer equivalent line is assigned a line number, and the three-phase true value of the voltages and currents of each line is saved in the files named as line_(line number)_true_3_phase.mat; the true positive sequence values are saved in the files named as line_(line number)_true_positive_sequence.mat in the format of [from-bus voltages, from-bus currents, to-bus voltages, to-bus currents]; the positive sequence values added errors are referred to as measured value and are saved in the files named as line_(line number)_measured_positive_sequence.mat with the same format as true value files; the total line number is 129 in the test case.

- Run True_impedance_calculation_IEEE_118.m through Matlab to acquire 345KV transmission lines’ impedances and susceptances and assign such data to the 10th and 11th column of AC_line_info.mat respectively and save the AC_line_info matrix in the file AC_line_info_true_value_Zy.mat.

- Copy the following files and paste it into the Step_3_Impedance Calibration folder: AC_line_info_true_value_Zy.mat,

Bus_number_set_345KV.mat,

line_(every linenumber)_measured_positive_sequence.mat,

line_(every line number)_true_positive_sequence.mat,

line_(every line number)_true_3_phase.mat (optional),

line_bus_info_345KV.mat.

## Transmission Line Impedance Calibration

In this section, the transmission line impedance calibration is conducted based on the simulated data throughout the 345KV subsystem within the IEEE 118 system.

- Locate in to the folder maned as Step_3_Impedance Calibration. Run line_parameter_estimation_IEEE_118.m through Matlab to start the impedance calibration process; notice that only run the following part of the code at the first time of the tests based on the same accurate bus to save the original voltage and current data of that bus and corresponding line.

%----------------------------------------------------%

line_name=['line_',num2str(original_accurate_line_number), '_measured_positive_sequence.mat'];

VI_origin_struct=load(line_name);

VI_measurement_set = VI_origin_struct.VI_measurement_set;

line_name=['line_',num2str(original_accurate_line_number),'_measured_positive_sequence_origin.mat'];

save(line_name,'VI_measurement_set');

%----------------------------------------------------%

- The Results are saved in the file named as line_estimation_results.mat in the form of [line number, from bus number, KV1_hat, KI1_hat, to bus number, KV2_hat, KI2_hat, Z_hat, y_hat], and the errors of the calibration are shown in the command window of Matlab as follow:

| line_number | KV1_error | KI1_error | KV2_error | KI2_error | Z_pu_error |
| --- | --- | --- | --- | --- | --- |
| ___________ | ____________________ | ___________________ | ____________________ | ___________________ | ____________________ |
| 10 | 0+0i | 0+0i | -8.9665e-08+6.4759e-08i | 3.3729e-05+0.00031885i | -3.875e-06-2.2941e-06i |
| 9 | -9.354e-07-8.6411e-08i | -0.054176-0.00059463i | -2.5268e-07+5.4999e-07i | -0.053696-0.0020156i | 5.0668e-05+0.00091915i |
| 6 | -1.4385e-06+5.4042e-07i | -0.048562-0.003765i | -0.00011939+3.0773e-05i | -0.048432-0.0062498i | -9.3247e-05+0.0049665i |
| 8 | -1.0321e-06+4.2567e-07i | -0.039879-0.090114i | 2.2211e-05-7.1517e-06i | -0.041844-0.090051i | -0.0028379+0.0012278i |
| 5 | -0.0001226+2.5583e-05i | 0.022484+0.054404i | -0.00010721+3.6383e-05i | 0.023412+0.054581i | -0.0029328-0.0010324i |
| 7 | 2.1753e-05-6.4653e-06i | -0.041025-0.085287i | -1.9731e-05-1.0317e-05i | -0.039203-0.10122i | -0.0019038+0.0008451i |
| 2 | -0.00010823+2.8655e-05i | 0.022379+0.085188i | -0.00012491+4.5585e-05i | 0.023679+0.087327i | -0.0042015-0.0010638i |
| 4 | -0.0001055+3.0809e-05i | -0.0077874+0.011213i | -0.00010639+5.3453e-05i | -0.0077156+0.011843i | -0.0009939+0.0007427i |
| 1 | -0.00012286+5.0807e-05i | -0.023302-0.021114i | -0.00011483+4.8006e-05i | -0.022492-0.021357i | -0.00057764+0.00075118i |
| 3 | -0.00011492+5.251e-05i | -0.021822-0.021623i | -0.0001167+6.4248e-05i | -0.022818-0.019937i | -0.00061303+0.00080305i |

Note: For some of the lines in IEEE 118 bus system, there are generators that connect to the relevant buses directly, which is not feasible in real-world power system. There is a good reason to believe that such scenario that generator -> line -> bus -> line -> bus connection should has negative influence to the estimation accuracy. Besides, given the propagation process, the estimation error of the previous pi-section will surely affect the consecutive ones, i.e. accumulation effect of the errors. Therefore, the later the lines are visited, the larger the estimation errors will be. For the further versions of the application, the algorithms will be improved to provide more accurate results.