## Slide 1
Working with openXDA

## Slide 2: Objective
To provide a deep dive into openXDA’s components and constructs to demonstrate openXDA’s adaptability and ease of addition of new processes.

## Slide 3: Overview

## Slide 4: What is openXDA?
A back-office automated service to automatically process and analyze event and trending data from transmission and distribution metering – DFRs and PQ metering

## Slide 5: openXDA – PQ / DFR Dualism
PQ – Largely distribution focused
  Single line monitoring
  Self-describing configuration in PQDIF
  Data may be collected by MDM systems
  Event and trending data
DFR – Largely transmission focused
  Multiple lines monitored
  Meter configuration information (channel mapping) required
  Only event data, typically as COMTRADE files

## Slide 6: openXDA Components
Installer for the openXDA service
Core service (includes File Watcher, logging and notification components)
Administrator’s remote console
Database (MS SQL Server)
Configuration management / loader tools

## Slide 7: openXDA Overview
openXDA Data

## Slide 8: openXDA Inputs
Configuration Data
  Meter name and location
  Meter channel definitions
  Line parameters
Waveform Data
  COMTRADE
  PQDIF
  EMAX (native format)
  SEL .eve (SEL-251, SEL-351, Sel-421 relays)

## Slide 9: Event Data
Time Domain
  Event attributes
  Event segments attributes
  Waveform
Frequency Domain
  Cycle data – Full-set of RMS and synchronous component values for each full cycle of data on the waveform
openXDA Data

## Slide 10: Event Analysis Data
Sags/Swells
  Duration
  Magnitude
Faults
  Type
  Inception time
  Duration
  Distance
  Prefault current
  Fault current
  Postfault current
openXDA Data

## Slide 11: Trending Data
Daily Values
  Min, Max, Average
Hourly Values
  Min, Max, Average
Full Resolution Values
  Min, Max, Average
openXDA Data

## Slide 12: Trending Alarm Data
Data Quality – Engineering reasonableness
  Latched
  Unreasonable (high/low limits)
  Incongruent (max > average > min)
Off-Normal – Hour-of-week 3 sigma excursions
Custom Alarms
openXDA Data

## Slide 13: openXDA Outputs
Analytic results saved in data base
Automated notifications
COMTRADE
  Line centric
  Includes both input and analytics cycle data

## Slide 14: COMTRADE Output is Line Centric

## Slide 15: Version 1.3 Example Email

## Slide 16: openXDA Remote Admin Console
Real-time monitoring of status log
Interact with service through commands

## Slide 17: openXDA Logging
Text File-Based Logging
  Status Log (key messages)
  Error Log
    Assembly, class, method
    Stack trace
    Exception type and message
  Debug Log – All status, most error and copious additional messages
DB Logging
  For analytics, easily searchable/reportable record of files processed and errors encountered

## Slide 18: What is the open PQ Dashboard?
The presentation layer PQ data housed in openXDA.
The openPQ Dashboard has been primarily funded by EPRI with extensions and contributions provided by others.

## Slide 19: Event Data Display
Selectable
Views
Powerful Date
Controls
Event Count Heat Map
Event Type
Site Location
Event Count and
Type by Date
Event Count and
Type by Site for
Selected Date
Link to
Event Detail
Version 0.7

## Slide 20: Fault Data Display
Selectable
Views
Powerful Date
Controls
Fault Count
By Site
Fault Count
By kV CLASS
Fault Summary
By Time for
Date Range
Links to
Fault Detail
Version 0.7

## Slide 21: Fault Waveform Detail
Fault Distance Calculation
Over the entire fault
Instantaneous,
RMS, Phasor Curves
Select Fault
And Event Time
Zoom / Scroll Axis
Values Displayed at Cursor Location
Select Any Event
From Specified Date

## Slide 22: Fault Detail Report

## Slide 23: Trending Data Display
Version 0.7

## Slide 24
Provides a separate Windows service platform for analytics based on the openXDA database.
Designed with integration in mind. Write analytics on another platform, such as Matlab, and integrate the results into openXDA.
Distributing analytics to separate Windows services allows for sandboxing analytics to prevent potentially unsafe code from compromising the openXDA platform.

## Slide 25: PQ Investigator Integration
PQ Investigator tolerance curves indicate the failure points of equipment based on voltage magnitude and duration.
Automatically determine after an event, such as a voltage sag, what equipment might have been affected by the disturbance.
View the list of affected equipment in the PQ Dashboard.

## Slide 26: PQ Investigator Integration

## Slide 27: The Deep Dive

## Slide 28: openXDA is an Automation Platform

## Slide 29: Highlight 1
The processes executed by openXDA are database driven.

## Slide 30: openXDA Constructs
ConfigurationLoader
  Load configuration updates from configuration source
DataReader
  Read data from files
DataOperation
  Perform data analysis and load results into database
DataWriter
  Provide results and notifications to external systems

## Slide 31: openXDA Inputs
Configuration Data
  Meter name and location
  Meter channel definitions
  Line parameters
Waveform Data
  COMTRADE
  PQDIF
  EMAX (native format)
  SEL .eve (SEL-251, SEL-351, Sel-421 relays)

## Slide 32: openXDA Event and Soft Configuration Data
MS SQL server required (2012 or later)
Easy to understand collection of tables with procedural interface layer
openXDA Data

## Slide 33: ConfigurationLoader
The ConfigurationLoader interface allows you to…
  Automatically load configuration from an external configuration data source on a timer
  Manually load configuration via the remote system console

## Slide 34: ConfigurationLoader
IConfigurationLoader interface

## Slide 35: ConfigurationLoader
Example ConfigurationLoader

## Slide 36: ConfigurationLoader

## Slide 37: Highlight 2
A console application can be used to remotely monitor and control the openXDA service.

## Slide 38: Console Commands

## Slide 39: ConfigurationLoader
Manual configuration load

## Slide 40: ConfigurationLoader
By default, openXDA automatically loads configuration once per day. This behavior can be modified via the remote system console. See the following link for details about the syntax for scheduling.
https://www.gridprotectionalliance.org/NightlyBuilds/GridSolutionsFramework/Help/html/T_GSF_Scheduling_Schedule.htm

## Slide 41: ConfigurationLoader
Reschedule automatic configuration load to once per hour instead of once per day.

## Slide 42: DataReader
The DataReader allows you to transform data from a file into a MeterDataSet that can be used by openXDA analytics.

## Slide 43: DataReader
IDataReader interface

## Slide 44: DataReader
Example COMTRADE file

## Slide 45: DataReader
CanParse() method (COMTRADEReader)

## Slide 46: DataReader
Parse() method (COMTRADEReader)
snip...

## Slide 47: DataReader

## Slide 48: Highlight 3
Robust file watcher detects new files dropped by source devices as soon as they are available.

## Slide 49: DataReader
FileExtension
  DataReaders are created and invoked when the file watcher detects that a file has appeared on the file system. The type of the DataReader that is created is determined by the extension of the file that is detected by the file watcher.

## Slide 50: DataOperation
The DataOperation allows you to…
  Analyze data from a MeterDataSet to produce meaningful results.
  Load the results of analysis into the database.

## Slide 51: DataOperation
IDataOperation interface

## Slide 52: DataOperation
DataOperationBase

## Slide 53: DataOperation
Prepare
  Database work that needs to be done in preparation for the data operation to execute. An example would be validation of supporting database tables, such as the EventType table.
  Executed outside of any database transactions so that locking of database objects can be kept to a minimum. Excessive database locking can reduce performance and increase the risk of deadlocks.

## Slide 54: DataOperation
EventOperation prepares by loading event types into the EventType table, ensuring that all the necessary event types exist before executing the operation.
EventType table

## Slide 55: DataOperation
Execute
  This is where data analysis is performed, transforming the input data into results that can be loaded into the database.
  No database work is actually done here. Analysis is performed and results are stored in memory in preparation for the Load method.

## Slide 56: DataOperation
In the EventOperation, Events are loaded into m_eventTable, an in-memory data table that models the Event table in the database.

## Slide 57: DataOperation
Load
  Loads the results of analysis into the database.
  This method is executed in a transaction that may or may not span multiple separate DataOperations. Keep work here to a minimum in order to reduce database locking.

## Slide 58: DataOperation
EventOperation uses a BulkLoader object to load Event records from m_eventTable into the database.
snip...

## Slide 59: DataOperation

## Slide 60: TransactionOrder
Determines the order in which groups of DataOperations will be executed.
  DataOperations with the same transaction order will be executed as a group.
  Each group of DataOperations shares a transaction with each other (Load method).
  If one DataOperation in the group fails, all DataOperations fail!

## Slide 61: LoadOrder
Determines the order in which DataOperations in the same group will be executed.

## Slide 62: DataWriter
The DataWriter allows you to send the results of your analysis to external systems apart from openXDA.

## Slide 63: DataWriter
IDataWriter interface

## Slide 64: DataWriter
COMTRADEWriter
snip...

## Slide 65: COMTRADE Output

## Slide 66: DataWriter

## Slide 67: openXDA Outputs
DataOperation
  Performs analysis
  Analytic results saved in database
DataWriter
  Automated notifications (e-mail, …)
  File output consumable by other systems (COMTRADE, …)
  …
DataOperation vs DataWriter?

## Slide 68: DataResource
The DataResource allows you to share analytic results as well as analysis routines between DataOperations. Sharing analysis routines allows separate DataOperations to use the results of the analysis regardless of which DataOperations exist in the system.

## Slide 69: DataResource
IDataResource interface
DataResourceBase

## Slide 70: DataResource
How it works:
  DataOperation calls meterDataSet.GetResource().
  MeterDataSet creates an instance of the DataResource and calls IDataResource.Initialize().
  MeterDataSet stores the DataResource in a lookup table by type so that subsequent calls to meterDataSet.GetResource() will not run the analysis again.

## Slide 71: Event Data
Time Domain
  Event attributes
  Event segments attributes
  Waveform
Frequency Domain
  Cycle data – Full-set of RMS and synchronous component values for each full cycle of data on the waveform
openXDA Data

## Slide 72: DataResource
CycleDataResource transforms the data from the frequency domain to the time domain. Any DataOperation can use the transformed data, and the analysis will only be performed once.

## Slide 73: Trending Data
Daily Values
  Min, Max, Average
Hourly Values
  Min, Max, Average
Full Resolution Values
  Min, Max, Average
openXDA Data

## Slide 74: DataResource
The HourlySummaryOperation uses the TrendingDataSummaryResource to group minimum, maximum, and average values by time so that it can further group them by hour. The DailySummaryOperation does the same thing, but groups the trending data by day.

## Slide 75: Highlight 4
A system settings and logging pattern makes it easy to create and configure new openXDA modules.

## Slide 76: System Settings
System settings allow you to define settings in the database to configure your custom modules. System settings in openXDA are easy to use and can be changed at runtime.

## Slide 77: System Settings
The Setting table contains simple name/value pairs.

## Slide 78: System Settings
DeviceDefinitionsLoader defines system settings via annotated properties.

## Slide 79: System Settings
And that’s it!
The properties defined by the DeviceDefinitionsLoader are automatically populated based on the names of the properties, the annotations, and the data in the Setting table. This approach works with all the following constructs.
  ConfigurationLoader
  DataReader
  DataOperation
  DataWriter
  DataResource

## Slide 80: System Settings
Categorized settings
  Settings can be placed into categories for better organization. This can help to find settings via database queries, and it can also help to consolidate settings definitions in the source code.

## Slide 81: System Settings
Setting names are prefixed by their categories, separated by a ‘.’

## Slide 82: System Settings
Create a class that defines the settings category. Annotate the properties like you would with normal system settings.

## Slide 83: System Settings
Modify the configuration loader to annotate a property as a Category. Instantiate a member variable of the type that defines your settings category.

## Slide 84: openXDA Logging
Logging allows you to provide messages back to the user for introspection into your modules’ activities.
openXDA uses log4net as its framework for generating log messages. Messages go straight to the remote system console as well as the various log files produced by openXDA.

## Slide 85: openXDA Remote Admin Console
Real-time monitoring of status log
Interact with service through commands

## Slide 86: openXDA Logging
Text File-Based Logging
  Status Log (key messages)
  Error Log
    Assembly, class, method
    Stack trace
    Exception type and message
  Debug Log – All status, most error and copious additional messages

## Slide 87: openXDA Logging
Create an ILog object through which to log your messages, then call Log.Info() to log a message.

## Slide 88: openXDA Logging
Remote system console

## Slide 89: openXDA Logging
The status log logs the messages that are printed to the remote system console.

## Slide 90: openXDA Logging
The debug log provides additional information about log messages as well as more verbose logging.

## Slide 91: openXDA Logging
Log levels
  log4net provides a number of log levels that can be used to log messages. Four levels are typically used by openXDA.
    Log.Error() – Errors and exception handling
    Log.Warn() – Warning messages
    Log.Info() – Regular status messages
    Log.Debug() – Debug messages
  The remote system console displays different colors based on the log level.
    Error = Red
    Warning = Yellow
    Status = White
    Debug = Hidden
  Debug messages only appear in the debug log.

## Slide 92: Questions ??