Oscillatory Mode Characterization of PMU Measurements

Installation and User Guide

GPA Engagement Project — Task 1

Version 1.1  •  August 18, 2026

Grid Protection Alliance

# Contents

Contents	2

Introduction	3

System Requirements and Installation	3

Requirements	3

Installation	3

Quick Start	3

Command-Line Usage	3

Configuration Reference	4

Scheduled and Periodic Operation	5

Methodology	5

Processing Pipeline	5

Confidence Metric	5

Output Files	6

Interpreting Results	6

Troubleshooting	6

# Introduction

The oscillation analysis tool (oscillation_analysis.py) automatically retrieves historical synchrophasor (PMU) data from an openHistorian instance and characterizes the oscillatory behavior present across the monitored fleet. For each identified oscillatory mode it reports:

- Frequency (Hz) with variability bounds

- Damping ratio (%) with variability bounds

- Amplitude (RMS, in the engineering units of each signal type)

- Growth/decay trends of amplitude and damping over time

- Mode shape: relative amplitude and phase of every participating channel

- Temporal persistence and cross-channel observability

- A confidence metric that separates meaningful modes from noise and spurious detections

Persistent modes whose damping falls below a configurable threshold (default 5%) are flagged for engineering review. Detected disturbances (frequency excursions, voltage deviations, angle steps) are logged and excluded from ambient-mode statistics so that event transients do not skew the results. Real-time oscillation detection and alarming are addressed by a separate online process and are out of scope for this tool.

Data access: the tool uses the official openHistorian Python API (PyPI package openhistorian) over the SNAPdb data-services socket (default port 38402) with STTP metadata refresh (default port 7175).

# System Requirements and Installation

## Requirements

- Windows or Linux with Python 3.10 or later (developed and tested on Python 3.12)

- Network access to the openHistorian server: TCP ports 38402 (SNAPdb data) and 7175 (STTP metadata)

- Approximately 200 MB of disk per analysis run for plots and reports (less with plots disabled)

## Installation

From the project folder, create a virtual environment and install the dependencies:

python -m venv .venv

.venv\Scripts\pip install -r requirements.txt

The requirements.txt file lists: openhistorian, numpy, scipy, matplotlib.

# Quick Start

Analyze the most recent 30 minutes of data from the local historian (defaults: instance PPA, 5-minute analysis windows with 50% overlap):

.venv\Scripts\python oscillation_analysis.py

Each run creates a time-stamped folder under oscillation_results\ and prints a console summary of the identified modes. Open report.html in that folder for the complete shareable dashboard.

# Command-Line Usage

All parameters are available as command-line flags (run with --help for the complete list). Common invocations:

| Purpose | Command |
| --- | --- |
| Most recent 30 minutes (defaults) | python oscillation_analysis.py |
| Quick look at recent data | python oscillation_analysis.py --lookback-minutes 10 --window-seconds 120 |
| Specific historical range (UTC) | python oscillation_analysis.py --start 2026-08-18T02:00:00 --end 2026-08-18T02:30:00 |
| Continuous operation every 30 min | python oscillation_analysis.py --interval-minutes 30 |
| Remote historian / other instance | python oscillation_analysis.py --host 10.115.2.80 --instance PPA |
| Include current phasors | python oscillation_analysis.py --signal-types FREQ,VPHM,VPHA,IPHM,IPHA |
| List matching channels and exit | python oscillation_analysis.py --list-points |
| Show effective configuration | python oscillation_analysis.py --dump-config |
| Use a JSON configuration file | python oscillation_analysis.py --config config.json |
| Disable plots (fastest) | python oscillation_analysis.py --no-plots |

A JSON configuration file (see config.example.json) may set any parameter; explicit command-line flags take precedence over the file.

# Configuration Reference

Key parameters (defaults in parentheses reflect the delivered configuration):

| Parameter | Default | Description |
| --- | --- | --- |
| host / instance | localhost / PPA | openHistorian server address and instance name |
| lookback_minutes | 30 | Analysis span ending now when start/end are not given |
| interval_minutes | 0 | If > 0, rerun continuously at this period |
| signal_types | FREQ,VPHM,VPHA | Signal types retrieved and analyzed |
| window_seconds | 300 | Analysis window length (spec: 5–10 minutes) |
| window_overlap | 0.5 | Fractional overlap between windows |
| fs_target | 10 | Decimation target sample rate (Hz) |
| f_min / f_max | 0.08 / 3.0 | Frequency band of engineering interest (Hz) |
| ar_order | 24 | Yule-Walker / Burg autoregressive model order |
| snr_min_db | 3.0 | Detection threshold at the mode frequency (dB) |
| event_exclusion | true | Exclude event windows from ambient statistics |
| event_freq_dev_hz | 0.05 | Event trigger: ¦f − nominal¦ threshold (Hz) |
| event_rocof_hz_s | 0.10 | Event trigger: ROCOF threshold on 1-s smoothed frequency (Hz/s) |
| event_vmag_dev_pu | 0.03 | Event trigger: voltage magnitude deviation (per-unit) |
| remove_steps | true | Repair level-shift discontinuities (replay splices, angle resyncs) |
| poor_damping_pct | 5.0 | Damping alert threshold for persistent modes (%) |
| min_data_fraction | 0.6 | Minimum data availability to keep a channel |
| output_dir | oscillation_results | Root folder for run outputs |

# Scheduled and Periodic Operation

Two options support the periodic-processing requirement:

- Built-in loop: run with --interval-minutes 30 to re-analyze continuously at a fixed period from a console or service wrapper.

- Windows Task Scheduler: register a daily task, e.g. daily processing of the previous 30-minute window at 01:00:

schtasks /Create /SC DAILY /ST 01:00 /TN "PMU Oscillation Analysis" ^

/TR "C:\path\to\.venv\Scripts\python.exe C:\path\to\oscillation_analysis.py"

Each scheduled run writes an independent time-stamped results folder, so historical runs accumulate for long-term trend assessment (the structured results.json/CSV outputs are designed for downstream trending).

# Methodology

## Processing Pipeline

- Retrieval — chunked streaming reads of all selected points in a single pass over the SNAPdb socket (approximately 200,000 samples/s observed), with automatic clamping to the data span actually present in the archive.

- Quality screening — historian quality flags, spike rejection (robust z-score), interpolation of short gaps, per-channel availability thresholds, and repair of level-shift discontinuities (“de-jump”) such as replay-loop splices or PMU angle resyncs.

- Event screening — frequency deviation, smoothed ROCOF, voltage-magnitude deviation and angle-step detectors mark disturbance intervals; windows overlapping events beyond a configurable fraction are excluded from ambient-mode statistics.

- Conditioning — angle unwrap, magnitude normalization to per-unit, anti-aliased decimation to 10 Hz, and 0.05 Hz highpass to remove slow trends and angle drift.

- Frequency-domain analysis — Welch power spectral density per channel per analysis window, fleet median PSD by signal type, and a spectrogram for temporal-spectral context.

- Modal identification — Yule-Walker autoregressive estimation per channel/window yields mode frequency and damping ratio from the AR poles; amplitude is obtained by integrating the PSD around the mode frequency; an independent Burg AR fit provides a cross-method consistency check.

- Aggregation — detections are clustered by frequency across windows and channels; each cluster reports median/IQR statistics, persistence, observability, amplitude by signal type, growth/decay trends, and confidence.

- Fleet-wide assessment — for each dominant mode, averaged cross-spectra against a reference channel yield relative amplitude, relative phase, and coherence per channel (mode shape), plus a participation ranking.

## Confidence Metric

Every aggregated mode carries a confidence score in [0, 1]:

confidence = 0.35*SNR + 0.30*persistence + 0.20*method-consistency + 0.15*observability

- SNR: median signal-to-noise ratio at the mode frequency (saturates at 12 dB)

- Persistence: fraction of ambient analysis windows in which the mode was detected

- Method consistency: agreement between the independent Yule-Walker and Burg estimates of frequency and damping

- Observability: fraction of analyzed channels detecting the mode (saturates at 50%)

Modes with fewer than 3 detections or confidence below 30% are classified spurious-likely. Modes at or above 75% confidence are high-confidence; 50–75% moderate; 30–50% low. A persistent mode (persistence ≥ 50%) whose median damping is below the poor-damping threshold raises an engineering-review alert.

# Output Files

Each run writes oscillation_results\run_<UTC timestamp>\ containing:

| File | Contents |
| --- | --- |
| report.html | Self-contained dashboard: alerts, KPI summary, sortable mode table, amplitudes and trends, mode shapes, events, data quality, and all plots embedded in one shareable file |
| report.md | Markdown summary of the same content |
| results.json | Full structured results for downstream tooling and long-term trending |
| modes_summary.csv | One row per aggregated mode with all characteristics |
| window_modes.csv | Every per-channel per-window detection (trending raw material) |
| mode_shapes.csv | Relative amplitude/phase/coherence per channel for dominant modes |
| events.csv | Detected disturbance intervals with triggers |
| channels.csv | Per-channel data-quality statistics and inclusion status |
| plots\*.png | PSD overview, spectrogram, mode trends, polar mode shapes, participation, raw-data overview |
| analysis.log | Run log |

# Interpreting Results

- Damping ratio: values below ~5% for persistent modes warrant engineering attention; 5–10% merits monitoring; above ~10% is well damped. Ambient AR estimates are most accurate precisely in the poorly damped range that matters; heavily damped modes (> 10%) carry wider uncertainty but pose no stability concern.

- Confidence: prioritize review by confidence and persistence. A high-SNR, low-persistence detection is often a transient or forced oscillation burst; inspect the spectrogram and mode-trends plots.

- Mode shape: channels grouped near 0° relative phase oscillate together; groups near 180° apart oscillate against each other. Coherence near 1.0 indicates the phase/amplitude estimate is reliable.

- Amplitude units: frequency modes in Hz, angle modes in degrees, magnitude modes in per-unit of each channel's median level.

# Troubleshooting

| Symptom | Resolution |
| --- | --- |
| “No data returned for the requested range” | The archive does not extend that far back. Reduce --lookback-minutes or verify the historian is collecting data. |
| Connection refused on port 38402 | Verify the openHistorian service is running and the SNAPdb data services port is enabled/reachable (firewall). |
| Metadata refresh fails on port 7175 | Confirm the STTP internal data publisher port; override with --sttp-port if configured differently. |
| All windows flagged as event windows | Thresholds too tight for the data. Raise event thresholds, or lower sensitivity of exclusion via event_max_window_overlap; as a diagnostic, run with --no-event-exclusion. |
| Channels excluded for low availability | See channels.csv for per-channel statistics; lower min_data_fraction to retain sparse channels if appropriate. |
| Many high-damping, low-confidence modes | Normal for broadband ambient noise. Filter results by confidence ≥ 50% and damping ≤ 15% when reviewing. |
| Runs are slow with plots enabled | Use --no-plots for scheduled bulk processing; plots add several seconds per run. |

For methodology validation details, see test_modal_math.py (synthetic-signal checks of the Yule-Walker and Burg estimators). Utility scripts explore_historian.py (connectivity/metadata probe) and diagnose_events.py (event-threshold tuning) are included alongside the main tool.