## Slide 1: Synchronized Measurement Communications at Scale
WAMS-MCC Software Training Meeting
J. Ritchie Carroll
Dec 3, 2024
Streaming Telemetry Transport Protocol
2664
IEEE C37.118
Synchrophasor Protocols

## Slide 2: Where in the Stack?
TRANSPORT: TCP / UDP (Internet Protocols)
  Foundational Base Layer
DATA: IEEE C37.118 / IEEE 2664/STTP (Synchrophasor Protocols)
  Data Transfer Layer
APPLICATION: PDC functions / Archiving Functions (openHistorian Tools)
  User Operation Layer

## Slide 3: What is a “Stream” of Data?
A stream of data is series of packets that are transmitted continuously from a publisher to a subscriber
Single Packet

## Slide 4: IEEE C37.118 Common Header
Each frame type in IEEE C37.118 have a common header
This defines a marker, the frame size, the ID code and the timestamp of the frame
The “SOC” is the second of century, since 1/1/1970
The “FRACESEC” is the fraction of the second needed for high resolution timestamps

## Slide 5: IEEE C37.118 Config Frame
The “Configuration Frame” contains the counts, labels, types and other details of what will come in data frames
This is the metadata of the stream
This frame is only needed once to parse data frames

## Slide 6: IEEE C37.118 Data Frame
The “Data Frames” represent the stream of data
These are “measured values” representing the synchrophasor data

## Slide 7: What Makes STTP Different?
Synchronized Frames vs Atomic Packets
Reduced Data Loss
Lossless Compression
Scalability (to hardware limits)
Publish / Subscribe Model
Publisher Data Access Control
IP Level Security
Configurable Connection Origin

## Slide 8: Difference: Synchronized Frames vs Atomic Packets
IEEE C37.118 / IEC 61850-90-5
MTU Fragment
MTU Fragment
MTU Fragment
STTP
MTU
MTU
Synchronized Frame of Measurements with Fixed Configuration
Individual Measurements
1 Packet, Several Unsynchronized Measurements
Measurements in one packet may differ from another
STTP Commands

## Slide 9: Difference: Reduced Data Loss
Data from testing performed at PeakRC
Transmitting Data with Small Atomic Packets and no Concentration Reduces Data Loss
STTP
Notes: Less data loss (no data loss with the preferred TCP)
Lower bandwidth requirements with TCP – lower than C37.118 UDP – using simple compression. That’s the bar by the green arrow. (BTW one of the goals of STTP is to improve upon this lossless compression – we hope significantly)
The curious thing about the data loss chart is that there is data loss with C37.118 even using TCP – why? (lagtime)

## Slide 10: Difference: Lossless Compression
IP based connections use TCP for commands and optionally UDP for data transmission:
  TCP provides reliable communications allowing for high-yield stateful compression
  UDP can be used for data transmission with the potential for UDP data loss and with less compression than TCP*
* Methods to implement STTP in Unicast/Multicast only configurations will be documented for use cases where a “no command” based STTP may represent a preferred option over Unicast/Multicast IEEE C37.118.
Lower Bandwidth with Lossless TCP
Compression
STTP

## Slide 11: Difference: Scalability
STTP handles from 3 to 5 million points per second per connection on common hardware.
Existing protocols
have 65K frame size limit setting max throughput to ~200 K pts/sec
per stream
Increased data loss and latency. Purpose-built / allocated networks typically required
Issues, if any, are easy to resolve
Data loss and latency issues begin to appear. Network tuning may be required
IEEE C37.118 V1 & V2 configuration frame size max out (65K). A second stream must be created
STTP Scales to Hardware Limits

## Slide 12: Difference: Publish / Subscribe Model
A-Data (Priority 1)
B-Data (Priority 2)
Metadata
Individual Data Point
Publisher
Subscriber
The STTP data is interleaved
Only data intended for subscriber will be published
ROUTING PROCESSOR
Notes: Data throughput is managed by interleaving published data over the socket
Interleaving is accomplished by placing non-contiguous data points into packets for publication
This interleaving is not only applied to data, but also metadata, to ensure that no one source of data will “consume the pipe”
Optionally STTP provides a simple level of publisher routing priority to provide some precedence for subscriber indicated data importance

## Slide 13: Difference: Publisher Data Access Control
Measurement 2
Measurement 1
Measurement 3
Measurement 4
All Source Measurements
Measurement 6
Measurement 5
STTP Publisher
STTP Subscriber A
STTP Subscriber B
Green or Blue Measurements
Green or Yellow Measurements

## Slide 14: STTP Difference: IP Level Security
Security at IP Layer
  TCP: Primary security is added at the socket using industry standard Transport Layer Security (TLS or SSL). X.509 certificates are used to authenticate connections and provide encryption through public key infrastructure.
  UDP (optional): When existing command channel is secured with TLS, UDP uses AES symmetric encryption with keys exchanged over the TLS secure channel.

## Slide 15: STTP Difference: Configurable Connection Origin
Publisher and Subscriber operations are “functions” in STTP – not “objects”
As such, a publisher “sends” data and a subscriber “receives” data – always
Crossing Security Zone with Reverse Connection

## Slide 16: New IEEE Standard
Publish / Subscribe Model
Publisher Data Access Control
IP Level Security
Configurable Connection Origin
2664
Atomic Measurement Packets
Reduced Data Loss
Lossless Compression
Scalability (to hardware limits)
Standard is published! IEEE 2664-2024

## Slide 17: Protocol Improvements in the IEEE Standard
Added higher time precision options
Some commands simplified / key words changed / unused options dropped
Define Operational Modes now requires a publisher success response to accept proposed subscriber options. Options now include:
  Custom compression algorithms selection for data packet, buffer block, signal index cache and metadata
  Custom UDP cipher encryption algorithm selection
New commands:
  Get Primary Metadata Schema
  Get Signal Selection Metadata Schema
  Confirm Update Cipher Keys
Suggested Metadata for synchrophasors has been improved / standardized
Includes a recommended Publisher and Subscriber API

## Slide 18: API Status -- see: https://sttp.info
 | Subscriber | TSCC | Filter Expressions | Reverse Subscriber | Publisher | Reverse Publisher | TLS
GSF |  |  |  |  |  |  | 
C++ / C# |  |  |  |  |  |  | 
Go |  |  |  |  |  |  | 
Python |  |  |  |  |  |  | 
Rust |  |  |  |  |  |  | 
Ongoing progress on STTP API language targets…
Primary API language targets expected to be function complete by end of year with new standard features
Integration can begin now

## Slide 19: Various Open-Source Implementations Available